## Revision
V113
V114
V114_bis
V115
V116
V117
V118
V119
V120
V121 | 2015-06-10
V122 | 2015-08-29
V123 | 2017-02-03 | Completed the parameters in Seq 1 & 11 (no change to the PLC structure - just for documentation)
V124 | 2017-09-22 | New status fields in the Epics buffer for electrovalves, valves and heater1
V125 | 2018-01-26 | New status bits for analog signals
V126 | 2018-06-08 | New data from/to Gersemi
V127 | 2018-08-20 | New data to HNOSS PLC (General)
V128 | 2018-11-15 | New data (General) for cryomodule integration
V129 | 2018-11-20 | Added state of He exchaust change sequence.
V129 | 2019-05-02 | Added sequence parameters for the Cryomodule control
V130 | 2020-12-08 | Added magnet currents to be sent to Gersemi PLC

## Equipments
EPICS Dialog
Digital Input | [7 empty] | All the time :
EPICS -> PLC |  |  |  | PLC -> EPICS |  |  |  |  | Copy of input is the physical input
Type "Epi_to_Plc_DI" |  |  |  | Type "Plc_to_Epi_DI" |  |  |  | Normal mode :
DBX0.0 | Bool | cmdNorm | Set Normal | DBX0.0 | Bool | sForced | Copy of Normal/Forced mode (0=Normal / 1=Forced) |  | Copy of Calculate Input is the delay input
DBX0.1 | Bool | cmdForced | Set Forced | DBX0.1 | Bool | sInp | Copy of Input | Forced mode :
DBX0.2 | Bool | cmdSet | Set forced command | DBX0.2 | Bool | sProcInp | Copy of Calculate Input |  | Copy of Calculate Input is the Forced command
DBX0.3 | Bool | cmdRst | Reset forced command | DBX0.3 | Bool
DBX0.4 | Bool |  |  | DBX0.4 | Bool
DBX0.5 | Bool |  |  | DBX0.5 | Bool
DBX0.6 | Bool |  |  | DBX0.6 | Bool
DBX0.7 | Bool |  |  | DBX0.7 | Bool
Process Analog Input
EPICS -> PLC |  |  |  | PLC -> EPICS |  |  |  |  | sRdV is always the phisical input
Type "Epi_to_Plc_AI" |  |  |  | Type "Plc_to_Epi_AI"
DBX0.0 | Bool | cmdNorm | Set Normal | DBX0.0 | Bool | sForced | Copy of Normal/Forced mode (0=Normal / 1=Forced) |  | sSetV is always a copy of Manual value
DBX0.1 | Bool | cmdForced | Set Forced | DBX0.1 | Bool | sOR | Copy of OR status (0=OK / 1=Over-range)
DBX0.2 | Bool | cmdSet | Set forced command | DBX0.2 | Bool | sUR | Copy of UR status (0=OK / 1=Under-range)
DBD2 | Real | cSetV | Manual Value | DBD2 | Real | sRdV | Process Value
|  |  |  | DBD6 | Real | sRealRdV | Real Process Values (as read from the input)
Valves | [7 empty] | Automatic mode :
EPICS -> PLC |  |  |  | PLC -> EPICS |  |  |  |  | Command is controled by program
Type "Epi_to_Plc_Valve" |  |  |  | Type "Plc_to_Epi_Valve" |  |  |  | Manual mode :
DBX0.0 | Bool | cmdAuto | Set Auto | DBX0.0 | Bool | sAuto | Copy of Auto/Manual mode (1=Auto / 0=Manual) |  | Command is controled by manual command
DBX0.1 | Bool | cmdMan | Set Manual | DBX0.1 | Bool | sSim | Copy of Simulation mode (1=Simulation)
DBX0.2 | Bool | cmdSet | Set manual command | DBX0.2 | Bool | sCmd | Copy of Command | Inhibition mode :
DBX0.3 | Bool | cmdRst | Reset manual command | DBX0.3 | Bool | sOn | Copy of On sensor(in Normal mode) - Simulated (in Simulation mode) |  | Faults are disable and sensor are simulated
DBX0.4 | Bool | cmdAck | Set Acknoledge | DBX0.4 | Bool | sOff | Copy of Off sensor(in Normal mode) - Simulated (in Simulation mode)
DBX0.5 | Bool | cmdSimSet | Set Simulation mode | DBX0.5 | Bool | sNO | Type of valve (0=Normally Closed - 1=Normally Open)
DBX0.6 | Bool | cmdSimRst | Reset Simulation mode | DBX0.6 | Bool | sOnFlt | Copy of fault On
DBX0.7 | Bool |  |  | DBX0.7 | Bool | sOffFlt | Copy of fault Off
|  |  |  | DBX1.0 | Bool | sFlt | LogicalsSum of sOnFlt and sOffFlt
|  |  |  | DBX1.1 | Bool | sCmdAuto | Copy of command in Auto mode
Electrovalves | [7 empty] | Automatic mode :
EPICS -> PLC |  |  |  | PLC -> EPICS |  |  |  |  | Command is controled by program
Type "Epi_to_Plc_EV" |  |  |  | Type "Plc_to_Epi_EV" |  |  |  | Manual mode :
DBX0.0 | Bool | cmdAuto | Set Auto | DBX0.0 | Bool | sAuto | Copy of Auto/Manual mode (1=Auto / 0=Manual) |  | Command is controled by manual command
DBX0.1 | Bool | cmdMan | Set Manual | DBX0.1 | Bool | sCmd | Copy of Command
DBX0.2 | Bool | cmdSet | Set manual command | DBX0.2 | Bool | sCmdAuto | Copy of command in Auto mode
DBX0.3 | Bool | cmdRst | Reset manual command | DBX0.3 | Bool
DBX0.4 | Bool |  |  | DBX0.4 | Bool
DBX0.5 | Bool |  |  | DBX0.5 | Bool
DBX0.6 | Bool |  |  | DBX0.6 | Bool
DBX0.7 | Bool |  |  | DBX0.7 | Bool
Analog Valves | [7 empty] | Automatic mode :
EPICS -> PLC |  |  |  | PLC -> EPICS |  |  |  |  | Output value is controled by program
Type "Epi_to_Plc_AnaValve" |  |  |  | Type "Plc_to_Epi_AnaValve" |  |  |  | Manual mode :
DBX0.0 | Bool | cmdAuto | Set Auto | DBX0.0 | Bool | sAuto | Copy of Auto/Manual mode (1=Auto / 0=Manual) |  | Output value is controled by manual value
DBX0.1 | Bool | cmdMan | Set Manual | DBX0.1 | Bool
DBX0.2 | Bool | cmdSet | Set manual command | DBX0.2 | Bool
DBD2 | Real | cSetV | Manual Value | DBD2 | Real | sRdV | Output Value
|  |  |  | DBD6 | Real | sAutoRdV | Automatic value
PID | [7 empty] | Auto mode :
EPICS -> PLC |  |  |  | PLC -> EPICS |  |  |  |  | Output mode is set to Automatic
Type "Epi_to_Plc_PID" |  |  |  | Type "Plc_to_Epi_PID" |  |  |  |  | Output value is controled by regulator with automatic Setpoint
DBX0.0 | Bool | cmdAuto | Set Auto (controlled by PLC) | DBX0.0 | Bool | sAuto | Copy of Auto/manual mode (1=Auto / 0=Manual) | Manual mode :
DBX0.1 | Bool | cmdMan | Set Norm (controlled by the operator) SPV ) | DBX0.1 | Bool | sRegOn | Copy of RegulatorOn/RegulatorOff mode (1=RegulatorOn / 0=RegulatorOff) |  | Operator can change Output mode
DBX0.2 | Bool | cmdRegOn | Set Output from setpoint via PID regulator | DBX0.2 | Bool | sAnalogSP | Copy of Analog Set-point (1 - analog setpoint, 0 - setpoint A (MKS only) |  | Output mode in RegulatorOn :
DBX0.3 | Bool | cmdRegOff | Set Output from local Output | DBX0.3 | Bool |  |  |  |  | Output value is controled by regulator with Local Setpoint
DBX0.4 | Bool | cmdSetP | Set Local Setpoint | [5 empty] | Output mode in RegulatorOff :
DBX0.5 | Bool | cmdOutput | Set Local Output | DBD2 | Real | sSetP | Actual setpoint |  |  | Output value is controled by Local Output
DBX0.6 | Bool | cmdASPon | Set Aanlog Set-poin (MKS only) | DBD6 | Real | sOutV | Actual Output
DBX0.7 | Bool | cmdASPoff | Reset Abalog Set-point (MKS only) | DBD10 | Real | sKp | Gain
DBD2 | Real | cSetP | Local Setpoint | DBD14 | Real | sTi | Integral time
DBD6 | Real | cOutput | Local Output | DBD18 | Real | sTd | Derived time
Heater (type 1) | [7 empty] | Automatic mode :
EPICS -> PLC |  |  |  | PLC -> EPICS |  |  |  |  | Command is controled by program
Type "Epi_to_Plc_Heater" |  |  |  | Type "Plc_to_Epi_Heater" |  |  |  | Manual mode :
DBX0.0 | Bool | cmdAuto | Set Auto | DBX0.0 | Bool | sAuto | Copy of Auto/Manual mode (1=Auto / 0=Manual) |  | Command is controled by manual command
DBX0.1 | Bool | cmdMan | Set Manual | DBX0.1 | Bool | sTsw | Copy of Thermoswitch
DBX0.2 | Bool | cmdSet | Set manual command | DBX0.2 | Bool | sCmd | Copy of command | All times :
DBX0.3 | Bool | cmdRst | Reset manual command | DBX0.3 | Bool | sCmdAuto | Copy of command in Auto mode |  | If Thermoswitch is ON then command is disable.
DBX0.4 | Bool | cmdHL | Set High limit | DBX0.4 | Bool | sHtrOn | State of the heater (in versions <123 sCmd behaved as this bit now)
DBX0.5 | Bool | cmdLL | Set Low Limit | DBX0.5 | Bool
DBX0.6 | Bool |  |  | DBX0.6 | Bool
DBX0.7 | Bool |  |  | DBX0.7 | Bool
DBD2 | Real | cHL | High limit | DBD2 | Real | sHL | State High limit
DBD6 | Real | cLL | Low Limit | DBD6 | Real | sLL | State Low Limit
Heater (type 2) | [7 empty] | Automatic mode :
EPICS -> PLC |  |  |  | PLC -> EPICS |  |  |  |  | Commands (1, 2 & 3) are controled by program
Type "Epi_to_Plc_Heater2" |  |  |  | Type "Plc_to_Epi_Heater2" |  |  |  | Manual mode :
DBX0.0 | Bool | cmdAuto | Set Auto | DBX0.0 | Bool | sAuto | Copy of Auto/Manual mode (1=Auto / 0=Manual) |  | Commands (1, 2 & 3) are controled by manuals commands (1, 2 & 3)
DBX0.1 | Bool | cmdMan | Set Manual | DBX0.1 | Bool | sTsw | Copy of Thermoswitch
DBX0.2 | Bool | cmdSet1 | Set manual command 1 | DBX0.2 | Bool | sCmd1 | Copy of command 1 | All times :
DBX0.3 | Bool | cmdRst1 | Reset manual command 1 | DBX0.3 | Bool | sCmd2 | Copy of command 2 |  | If Thermoswitch is ON then commands are disable.
DBX0.4 | Bool | cmdSet2 | Set manual command 2 | DBX0.4 | Bool | sCmd3 | Copy of command 3
DBX0.5 | Bool | cmdRst2 | Reset manual command 2 | DBX0.5 | Bool | sLs | Copy of Water Level switch
DBX0.6 | Bool | cmdSet3 | Set manual command 3 | DBX0.6 | Bool | sHtrOn | Copy of Input Heater On
DBX0.7 | Bool | cmdRst3 | Reset manual command 3 | DBX0.7 | Bool | sSim | Copy of Simulation mode (1=Simulation)
DBX1.0 | Bool | cmdAck | Set Acknoledge | DBX1.0 | Bool | sFlt | Copy of fault
DBX1.1 | Bool | cmdSimSet | Set Simulation mode
DBX1.2 | Bool | cmdSimRst | Reset Simulation mode
DBX1.3 | Bool | cmdL1 | Set limit 1
DBX1.4 | Bool | cmdL2 | Set limit 2
DBX1.5 | Bool | cmdL3 | Set limit 3
DBX1.6 | Bool
DBX1.7 | Bool
DBD2 | Real | cL1 | limit 1 | DBD2 | Real | sL1 | limit 1
DBD6 | Real | cL2 | limit 2 | DBD6 | Real | sL2 | limit 2
DBD10 | Real | cL3 | limit 3 | DBD10 | Real | sL3 | limit 3

## Sequences
Sequences |  |  |  | SQ0 |  | SQ1 |  | SQ2 |  | SQ3A |  | SQ3B |  | SQ4 |  | SQ5 |  | SQ6 |  | SQ7 |  | SQ8 |  | SQ9 |  | SQ10 |  | SQ11 |  | SQ12A |  | SQ12B |  | SQ13 |  | SQ20
EPICS -> PLC |  |  |  | Parameter | Comment | Parameter | Comment | Parameter | Comment | Parameter | Comment | Parameter | Comment | Parameter | Comment | Parameter | Comment | Parameter | Comment | Parameter | Comment | Parameter | Comment | Parameter | Comment | Parameter | Comment | Parameter | Comment | Parameter | Comment | Parameter | Comment | Parameter | Comment | Parameter | Comment
Type "Epi_to_Plc_Seq"
DBX0.0 | Bool | cmdStart | Start - Command
DBX0.1 | Bool | cmdStop | Stop - Command
DBX0.2 | Bool | cmdPause | pause - Command | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable
DBX0.3 | Bool | cmdResume | Resume - Command | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable
DBX0.4 | Bool | cmdReset | Reset - Command
DBX0.5 | Bool | cmdAccept | Acceptation - Command
DBX0.6 | Bool | cmdSetParam | Write parameters - Commands
DBX0.7 | Bool | cmdSpare
DBX1.0 | Bool | cParB1 | Bool - Sequence parameter | [10 empty] | P_C1 | Parameter : Coupler 1 | cP_LIC100 | LIC100 pid controller (1 = ON, 0 = OFF) |  |  | P_C1 | Parameter : Cavity 1 | P_Ms | Parameter : Magnetic Shield | P_MS | Parameter : Magnetic Shield | P_C1 | Parameter : Coupler 1 | P_MS | Parameter : Magnetic Shield | P_MS |  |  |  | P_Isol_Cryo | Parameter : Isolation Cryostat (1=Cryostat isolated) | P_Cond_Cryo | Parameter : Conditionning Cryostat
DBX1.1 | Bool | cParB2 | Bool - Sequence parameter | [10 empty] | P_C2 | Parameter : Coupler 2 |  |  |  |  | P_C2 | Parameter : Cavity 2 | P_Tbl | Parameter : Table | P_Tbl | Parameter : Table | P_C2 | Parameter : Coupler 2 | P_TBL | Parameter : Table | P_Tbl | [5 empty] | P_Cond_Coupl | Parameter : Conditionning Couplers
DBX1.2 | Bool | cParB3 | Bool - Sequence parameter | [10 empty] | P_Tt | Parameter : Temperature Order |  |  |  |  | P_Tbl | Parameter : Table | cP_LIC101 | LIC101A pid controller (1 = ON, 0 = OFF) | cP_LIC101 | LIC101B pid controller (1 = ON, 0 = OFF) | P_Tt | Parameter : Temperature Order |  | Parameter : Cavity 1 | P_C1 | [5 empty] | P_Cooldown_Cryo | Parameter : Cool down Cryostat
DBX1.3 | Bool | cParB4 | Bool - Sequence parameter | [10 empty] | P_Ft | Parameter : Flow Order |  |  |  |  | P_MS | Parameter : Magnetic Shield |  |  |  |  | P_Ft | Parameter : Flow Order |  | Parameter : Cavity 2 | P_C2 | [5 empty] | P_SHe | Parameter : Supercritique Mode
DBX1.4 | Bool | cParB5 | Bool - Sequence parameter | [32 empty] | P_WarmUp_Cryo | Parameter : WarmUp Cryostat
DBX1.5 | Bool | cParB6 | Bool - Sequence parameter | [32 empty] | P_Isol_Cryo | Parameter : Cryostat Isolated
DBX1.6 | Bool | cParB7 | Bool - Sequence parameter | [32 empty] | P_Stop_Seq | Parameter : Stop Sequences
DBX1.7 | Bool | cParB8 | Bool - Sequence parameter
DBW2 | Int | cParI1 | Integer - Sequence parameter | P_Nb_Cycle | Parameter : Nomber of cycle to configure | P_Nb_Cycle | Parameter : Nomber of cycle to configure | P_Nb_Cycle | Parameter : Nomber of cycle to configure | [26 empty] | P_Ope_Cryo | Parameter : Operation Cryostat (1 = 4K ; 2 = 2K ; 3 = Stdy)
DBW4 | Int | cParI2 | Integer - Sequence parameter | P_Tempo_Vaccum | Parameter : Time of vaccum | P_Tempo_Vaccum | Parameter : Time of vaccum | P_Tempo_Vaccum | Parameter : Time of vaccum
DBW6 | Int | cParI3 | Integer - Sequence parameter | P_Tempo_Pressure | Parameter : Time of pressure | P_Tempo_Pressure | Parameter : Time of pressure | P_Tempo_Pressure | Parameter : Time of pressure
DBW8 | Int | cParI4 | Integer - Sequence parameter | P_Te_Al_Vaccum | Parameter : Time alarme vaccum | P_Te_Al_Vaccum | Parameter : Time alarme vaccum | P_Te_Al_Vaccum | Parameter : Time alarme vaccum
DBW10 | Int | cParI5 | Integer - Sequence parameter | P_Te_Al_Pressure | Parameter : Time alarme pressure | P_Te_Al_Pressure | Parameter : Time alarme pressure | P_Te_Al_Pressure | Parameter : Time alarme pressure
DBW12 | Int | cParI6 | Integer - Sequence parameter
DBW14 | Int | cParI7 | Integer - Sequence parameter
DBW16 | Int | cParI8 | Integer - Sequence parameter
DBW18 | Int | ReservedI9 | Integer - Sequence parameter | Not to be used by any sequence
DBD20 | Real | cParR1 | Real - Sequence parameter | P_Vacum | Parameter : Pressure Vacum | P_Vacum | Parameter : Pressure Vacum | P_Vacum | Parameter : Pressure Vacum | P_Tt | Parameter : Temperature for flow cooling | P_Tt | Parameter : Temperature for flow cooling | P_CV200_Tt | Parameter : Temperature Order for control CV200 | P_PT | Parameter : Warning Pressure | P_Tt | Parametre : Temperature Security | P_PT | Parameter : Warning Pressure | P_CV550 | Parameter : Valves Order | P_CV550 | Parameter : Valves Order | P_CV301_Tt | Parameter : Temperature Order for control CV301 | P_CV550 | Parameter : Valves Order | P_WarmUp | Parameter : Temperature to Warm-Up | P_WarmUp | Parameter : Temperature Warm-Up | P_Al_SHe | Parameter : Alarme Pressure SHe Circuit
DBD24 | Real | cParR2 | Real - Sequence parameter | P_FaultVacum | Parameter : Pressure Fault Vacum | P_FaultVacum | Parameter : Pressure Fault Vacum | P_FaultVacum | Parameter : Pressure Fault Vacum | P_Low_Tt | Parameter : Low Treshold cooling | P_Low_Tt | Parameter : Low Treshold cooling (EV200) in KELVIN | P_CV200_FT | Parameter : Flow Order for control CV200 | P_FT | Parameter : Warning Flow | P_Lt | Parametre : Level Security | P_FT550 | Parameter : Warning Flow | P_LowLt | Parameter : Low Level | P_LowLt | Parameter : Low Level | P_CV301_Ft | Parameter : Flow Order for control CV301 | P_Tt | Parameter : SetPoint Temperature |  |  | P_CV550 | Parameter : Valves Order (CV550) | P_Al_He | Parameter : Alarme Pressure He Circuit
DBD28 | Real | cParR3 | Real - Sequence parameter | P_Filling | Parameter : Pressure End Of Filling GHe | P_Filling | Parameter : Pressure End Of Filling GHe | P_Filling | Parameter : Pressure End Of Filling GHe | P_High_Tt | Parameter : High Treshold cooling | P_High_Tt | Parameter : High Treshold cooling (EV200) in KELVIN | P_CV201_Tt | Parameter : Temperature Order for control CV201 | P_CV550 | Parameter : Order valve |  |  | P_Tt_Cold | Parameter : Temperature to Keeping Cold equipment | P_HighLt | Parameter : High Level | P_HighLt | Parameter : High Level | P_CV302_Tt | Parameter : Temperature Order for control CV302 | P_Pt | Parameter : Warning Pressure |  |  | P_CV551 | Parameter : Valves Order (CV551) | P_SHe | Parameter : Pressure SHe Circuit
DBD32 | Real | cParR4 | Real - Sequence parameter | P_FaultF | Parameter : Pressure Fault Filling | P_FaultF | Parameter : Pressure Fault Filling | P_FaultF | Parameter : Pressure Fault Filling |  |  |  |  | P_CV201_Ft | Parameter : Flow Order for control CV201 | P_LowLt | Parameter : Low Level |  |  | P_SP_Tt | Parameter : SetPoint Control temperature | P_Pt | Parameter : Warning Pressure | P_Pt | Parameter : Warning Pressure | P_CV302_Ft | Parameter : Flow Order for control CV302 | P_SP_Tt | Parameter : SetPoint Control Temperature |  |  | P_CV552 | Parameter : Valves Order (CV552) | P_He | Parameter : Pressure He Circuit
DBD36 | Real | cParR5 | Real - Sequence parameter |  |  | P_CV100 | Parameter : Order for Analog Valves | P_CV301 | Parameter : Order for Analog Valves | [6 empty] | P_CoolD_Tt | Parameter : Temperature cool doawn |  |  | P_CV550 | Parameter : Valves Order | P_SP_Tt | Parameter : SetPoint Control Temperature | P_SP_Tt | Parameter : SetPoint Control Temperature |  |  | P_CV551 | Parameter : Valves Order |  |  | P_CV100 | Parameter : Valves Order (CV100)
DBD40 | Real | cParR6 | Real - Sequence parameter |  |  | P_CV101 | Parameter : Order for Analog Valves | P_CV302 | Parameter : Order for Analog Valves | [6 empty] | P_HighLt | Parameter : High Level |  |  | P_CV551 | Parameter : Valves Order | P_CV551 | Parameter : Valves Order | P_CV105 | Parameter : Valves Order |  |  | P_CV552 | Parameter : Valves Order |  |  | P_CV101 | Parameter : Valves Order (CV101)
DBD44 | Real | cParR7 | Real - Sequence parameter |  |  | P_CV102 | Parameter : Order for Analog Valves | [8 empty] | P_CV100 | Parameter : Order valve |  |  | P_FT552 | Parameter : Warning Flow | P_CV552 | Parameter : Valves Order | P_CV551_Reg | Parameter - Setpoint of regulation |  |  | P_CV104 | Parameter : Valves Order |  |  | P_CV102 | Parameter : Valves Order (CV102)
DBD48 | Real | cParR8 | Real - Sequence parameter |  |  | P_CV103 | Parameter : Order for Analog Valves | [8 empty] | P_SP_LIC100 | Set Point for LIC100 pid |  |  | P_HighLt | Parameter : High Level | P_CV104 | Parameter : Valves Order | P_Final_Pt | Parameter - Final Pressure |  |  |  | Parameter : Valves Order |  |  | P_CV103 | Parameter : Valves Order (CV103)
DBD52 | Real | cParR9 | Real - Sequence parameter |  |  | P_CV104 | Parameter : Order for Analog Valves | [12 empty] | P_LowLt | Parameter : Low Level | P_SP_LIC101 | Set Point for LIC101A pid | P_SP_LIC101 | Set Point for LIC101B pid | [6 empty] | P_CV104 | Parameter : Valves Order (CV104)
DBD56 | Real | cParR10 | Real - Sequence parameter |  |  | P_CV105 | Parameter : Order for Analog Valves | [12 empty] | P_CV552 | Parameter : Valves Order | [10 empty] | P_CV105 | Parameter : Valves Order (CV105)
DBD60 | Real | cParR11 | Real - Sequence parameter |  |  | P_CV550 | Parameter : Order for Analog Valves | [12 empty] | P_CV101 | Parameter : Valves Order | [10 empty] | P_CV200 | Parameter : Valves Order (CV200)
DBD64 | Real | cParR12 | Real - Sequence parameter |  |  | P_CV551 | Parameter : Order for Analog Valves | [12 empty] | P_CV102 | Parameter : Valves Order | [10 empty] | P_CV201 | Parameter : Valves Order (CV201)
DBD68 | Real | cParR13 | Real - Sequence parameter |  |  | P_CV552 | Parameter : Order for Analog Valves | [12 empty] | P_CV103 | Parameter : Valves Order | [10 empty] | P_CV302 | Parameter : Valves Order (CV302)
DBD72 | Real | cParR14 | Real - Sequence parameter | [16 empty] | P_CV104 | Parameter : Valves Order | [10 empty] | P_CV301 | Parameter : Valves Order (CV302)
DBD76 | Real | cParR15 | Real - Sequence parameter | [16 empty] | P_CM_PT551_SP | Parameter for the Cryomodule: MKS2 set-point for the PID
DBD80 | Real | cParR16 | Real - Sequence parameter
Sequences
PLC -> EPICS
Type "Plc_to_Epi_Seq"
DBX0.0 | Bool | sActivate | Activate - State
DBX0.1 | Bool | sRun | Run - State
DBX0.2 | Bool | sPause | Pause - State
DBX0.3 | Bool | sFault | Fault - State
DBX0.4 | Bool | sStop | Stop - State
DBX0.5 | Bool | sStopping | Stopping - State
DBX0.6 | Bool | sCIok | Initials conditions ok
DBX0.7 | Bool | sCSok | Security conditions ok
DBX1.0 | Bool | sFlt1 | Sequence Fault | Flt_Vaccum | Fault : Vaccum Alarm | Flt_Vaccum | Fault : Vaccum Alarm | Flt_Vaccum | Fault : Vaccum Alarm | [24 empty] | Flt_SHePres | Fault : Circuits SHe Pressure
DBX1.1 | Bool | sFlt2 | Sequence Fault | Flt_Pressure | Fault : Vaccum Alarm | Flt_Pressure | Fault : Vaccum Alarm | Flt_Pressure | Fault : Vaccum Alarm | [24 empty] | Flt_HePres | Fault : Circuits He Pressure
DBX1.2 | Bool | sFlt3 | Sequence Fault
DBX1.3 | Bool | sFlt4 | Sequence Fault
DBX1.4 | Bool | sFlt5 | Sequence Fault
DBX1.5 | Bool | sFlt6 | Sequence Fault
DBX1.6 | Bool | sCheckParam | Check Parameters
DBX1.7 | Bool | sCheckEquip | Check Equipment in manual mode
DBW2 | Int | sStep | Sequence Grafcet Step
DBW4 | Int | sStepTime | Temporisation of Sequence Grafcet Step | [6 empty] | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable
DBW6 | Int | sStateI1 | Integer - State indicator | Cpt_Nb_Cycle | Compteur : Actual Nomber of cycle | Cpt_Nb_Cycle | Compteur : Actual Nomber of cycle | Cpt_Nb_Cycle | Compteur : Actual Nomber of cycle
DBW8 | Int | sStateI2 | Integer - State indicator
DBD10 | Real | sStateR1 | Real - State indicator
DBD14 | Real | sStateR2 | Real - State indicator
DBX18.0 | Bool | sParB1 | Bool - Sequence parameter | Same as Epics to Plc commands parameters
DBX18.1 | Bool | sParB2 | Bool - Sequence parameter
DBX18.2 | Bool | sParB3 | Bool - Sequence parameter
DBX18.3 | Bool | sParB4 | Bool - Sequence parameter
DBX18.4 | Bool | sParB5 | Bool - Sequence parameter
DBX18.5 | Bool | sParB6 | Bool - Sequence parameter
DBX18.6 | Bool | sParB7 | Bool - Sequence parameter
DBX18.7 | Bool | sParB8 | Bool - Sequence parameter
DBW20 | Int | sParI1 | Integer - Sequence parameter
DBW22 | Int | sParI2 | Integer - Sequence parameter
DBW24 | Int | sParI3 | Integer - Sequence parameter
DBW26 | Int | sParI4 | Integer - Sequence parameter
DBW28 | Int | sParI5 | Integer - Sequence parameter
DBW30 | Int | sParI6 | Integer - Sequence parameter
DBW32 | Int | sParI7 | Integer - Sequence parameter
DBW34 | Int | sParI8 | Integer - Sequence parameter
DBW36 | Int | sInitCond | Sequence - Initials conditions
DBD38 | Real | sParR1 | Real - Sequence parameter
DBD42 | Real | sParR2 | Real - Sequence parameter
DBD46 | Real | sParR3 | Real - Sequence parameter
DBD50 | Real | sParR4 | Real - Sequence parameter
DBD54 | Real | sParR5 | Real - Sequence parameter
DBD58 | Real | sParR6 | Real - Sequence parameter
DBD62 | Real | sParR7 | Real - Sequence parameter
DBD66 | Real | sParR8 | Real - Sequence parameter
DBD70 | Real | sParR9 | Real - Sequence parameter
DBD74 | Real | sParR10 | Real - Sequence parameter
DBD78 | Real | sParR11 | Real - Sequence parameter
DBD82 | Real | sParR12 | Real - Sequence parameter
DBD86 | Real | sParR13 | Real - Sequence parameter
DBD90 | Real | sParR14 | Real - Sequence parameter
DBD94 | Real | sParR15 | Real - Sequence parameter
DBD98 | Real | sParR16 | Real - Sequence parameter

## General
General
EPICS -> PLC
Type "Epi_to_Plc_Gen"
DBX0.0 | Bool | cmdSetParam | Write parameters - Commands
DBX0.1 | Bool | CmdSetAck | Set General Acknoledge - Commands
DBX0.2 | Bool | cmdSet2KtoBaloon | Direct the 2K He recirculation to the Baloon
DBX0.3 | Bool | cmdRst2KtoBaloon | Direct the 2K He recirculation to the compressor
DBX0.4 | Bool | cmdSet4KtoBaloon | Direct the 4K He recirculation to the Baloon
DBX0.5 | Bool | cmdRst4KtoBaloon | Direct the 4K He recirculation to the compressor
DBX0.6 | Bool | cmdSetCMmode | Set Cryo-module mode
DBX0.7 | Bool | cmdRstCMmode | Reset Cryo-module mode (return to HNOSS mode)
DBX1.0 | Bool | Dwr:CW5202_open | Status of Linde's CV5202 1 -open, 0 - closed
DBX1.1 | Bool | Dwr:CW5201_open | Status of Linde's CV5201 1 -open, 0 - closed
DBX1.2 | Bool | PB_com_2Kpumps | Status of PB comm. to 2K pumps 1-OK, 0- error
DBX1.3 | Bool | WTRVAC_IOC | 1- connected, 0 - disconnected
DBX1.4 | Bool | WTRVAC_IOC_STAT | 1 - OK, 0 - error
DBX1.5 | Bool | cmdSetLocal | Set Local mode (WinCC control)
DBX1.6 | Bool | cmdSetRemote | Set Remote mode (Epics control)
DBX1.7 | Bool | cParB8 | Bool - Dialogue
DBW2 | Int | HBcounter | HeartBeat counter from Gersemi (updates at least every 10 s)
DBW4 | Int | HBcounter-ioc | HearBeat counter from HNOSS ioc
DBW6 | Int | PC1_Cur_SEVR | Severity status of MAG-RCH1:I_MEAS
DBW8 | Int | PC2_Cur_SEVR | Severity status of MAG-RCH2:I_MEAS
DBW10 | Int | cParI5 | Integer - Dialogue
DBW12 | Int | cParI6 | Integer - Dialogue
DBW14 | Int | cParI7 | Integer - Dialogue
DBW16 | Int | cParI8 | Integer - Dialogue
DBW18 | Int | cParI9 | Integer - Dialogue
DBD20 | Real | LI5200-PercOut | LHe level in the dewar
DBD24 | Real | LI3685-PercOut | LN2 level in the tank
DBD28 | Real | UY5202-PercOut | Percentage of opening of the dewar valve
DBD32 | Real | Freq_2K_pumps | Mean revol. Freq. of all 2K pumps Hz | Note: for this value to be trusted the following condition must be true:
DBD36 | Real | UY5201-PercOut | Percentage of opening of the dewar valve | (PB_com_2Kpumps = 1) & (WTRVAC_IOC = 1) & (WTRVAC_IOC_STAT = 1) & (HBcounter-ioc MUST change every 10 s)
DBD40 | Real | PC1_CURRENT | Magnet current MAG-RCH1:I_MEAS
DBD44 | Real | PC2_CURRENT | Magnet current MAG-RCH2:I_MEAS
DBD48 | Real | cParR8 | Real - Dialogue
DBD52 | Real | cParR9 | Real - Dialogue
DBD56 | Real | cParR10 | Real - Dialogue
DBD60 | Real | cParR11 | Real - Dialogue
DBD64 | Real | cParR12 | Real - Dialogue
DBD68 | Real | cParR13 | Real - Dialogue
DBD72 | Real | cParR14 | Real - Dialogue
DBD76 | Real | cParR15 | Real - Dialogue
DBD80 | Real | cParR16 | Real - Dialogue
General
PLC -> EPICS
Type "Plc_to_Epi_Gen"
DBX0.0 | Bool | sLocal | false - EPICS rules, true - WinCC is in charge
DBX0.1 | Bool | s2KtoBaloon | false compressor, true - gas baloon
DBX0.2 | Bool | s4KtoBaloon | false compressor, true - gas baloon
DBX0.3 | Bool | sCMmode | 1 - Cryo-module mode, 0 - HNOSS mode
DBX0.4 | Bool
DBX0.5 | Bool
DBX0.6 | Bool
DBX0.7 | Bool
DBX1.0 | Bool | sParB1 | Bool - Dialogue
DBX1.1 | Bool | sParB2 | Bool - Dialogue
DBX1.2 | Bool | sParB3 | Bool - Dialogue
DBX1.3 | Bool | sParB4 | Bool - Dialogue
DBX1.4 | Bool | sParB5 | Bool - Dialogue
DBX1.5 | Bool | sParB6 | Bool - Dialogue
DBX1.6 | Bool | sParB7 | Bool - Dialogue
DBX1.7 | Bool | sParB8 | Bool - Dialogue
DBW2 | Int | sGersemi_HB | Life_Word from Gersemi
DBW4 | Int | sState_4K_X | Step of the 4K exhaust change between compressor and gas bag
DBW6 | Int | sState_2K_X | Step of the 2K exhaust change between compressor and gas bag
DBW8 | Int | sParI4 | Integer - Dialogue
DBW10 | Int | sParI5 | Integer - Dialogue
DBW12 | Int | sParI6 | Integer - Dialogue
DBW14 | Int | sParI7 | Integer - Dialogue
DBW16 | Int | sParI8 | Integer - Dialogue
DBW18 | Int | sParI9 | Integer - Dialogue
DBD20 | Real | sParR1 | Real - Dialogue
DBD24 | Real | sParR2 | Real - Dialogue
DBD28 | Real | sParR3 | Real - Dialogue
DBD32 | Real | sParR4 | Real - Dialogue
DBD36 | Real | sParR5 | Real - Dialogue
DBD40 | Real | sParR6 | Real - Dialogue
DBD44 | Real | sParR7 | Real - Dialogue
DBD48 | Real | sParR8 | Real - Dialogue
DBD52 | Real | sParR9 | Real - Dialogue
DBD56 | Real | sParR10 | Real - Dialogue
DBD60 | Real | sParR11 | Real - Dialogue
DBD64 | Real | sParR12 | Real - Dialogue
DBD68 | Real | sParR13 | Real - Dialogue
DBD72 | Real | sParR14 | Real - Dialogue
DBD76 | Real | sParR15 | Real - Dialogue
DBD80 | Real | sParR16 | Real - Dialogue

## Parameters
Real Parameters |  |  |  | SQ9_CV551_PT |  | SQ9_CV551_Csg
EPICS -> PLC |  |  |  | Parameter | Comment | Parameter | Comment
Type "Epi_to_Plc_ParR"
DBD0 | Real | cParR0 | Real - Dialogue | PT00 | Pressure limit | Csg00 | Setpoint of analog valve
DBD4 | Real | cParR1 | Real - Dialogue | PT01 | Pressure limit | Csg01 | Setpoint of analog valve
DBD8 | Real | cParR2 | Real - Dialogue | PT02 | Pressure limit | Csg02 | Setpoint of analog valve
DBD12 | Real | cParR3 | Real - Dialogue | PT03 | Pressure limit | Csg03 | Setpoint of analog valve
DBD16 | Real | cParR4 | Real - Dialogue | PT04 | Pressure limit | Csg04 | Setpoint of analog valve
DBD20 | Real | cParR5 | Real - Dialogue | PT05 | Pressure limit | Csg05 | Setpoint of analog valve
DBD24 | Real | cParR6 | Real - Dialogue | PT06 | Pressure limit | Csg06 | Setpoint of analog valve
DBD28 | Real | cParR7 | Real - Dialogue | PT07 | Pressure limit | Csg07 | Setpoint of analog valve
DBD32 | Real | cParR8 | Real - Dialogue | PT08 | Pressure limit | Csg08 | Setpoint of analog valve
DBD36 | Real | cParR9 | Real - Dialogue | PT09 | Pressure limit | Csg09 | Setpoint of analog valve
DBD40 | Real | cParR10 | Real - Dialogue | PT010 | Pressure limit | Csg010 | Setpoint of analog valve
DBD44 | Real | cParR11 | Real - Dialogue | PT011 | Pressure limit | Csg011 | Setpoint of analog valve
DBD48 | Real | cParR12 | Real - Dialogue | PT012 | Pressure limit | Csg012 | Setpoint of analog valve
DBD52 | Real | cParR13 | Real - Dialogue
DBD56 | Real | cParR14 | Real - Dialogue
DBD60 | Real | cParR15 | Real - Dialogue
Real Parameters
PLC -> EPICS
Type "Plc_to_Epi_ParR"
DBD0 | Real | sParR0 | Real - Dialogue | PT00 | Pressure limit | Csg00 | Setpoint of analog valve
DBD4 | Real | sParR1 | Real - Dialogue | PT01 | Pressure limit | Csg01 | Setpoint of analog valve
DBD8 | Real | sParR2 | Real - Dialogue | PT02 | Pressure limit | Csg02 | Setpoint of analog valve
DBD12 | Real | sParR3 | Real - Dialogue | PT03 | Pressure limit | Csg03 | Setpoint of analog valve
DBD16 | Real | sParR4 | Real - Dialogue | PT04 | Pressure limit | Csg04 | Setpoint of analog valve
DBD20 | Real | sParR5 | Real - Dialogue | PT05 | Pressure limit | Csg05 | Setpoint of analog valve
DBD24 | Real | sParR6 | Real - Dialogue | PT06 | Pressure limit | Csg06 | Setpoint of analog valve
DBD28 | Real | sParR7 | Real - Dialogue | PT07 | Pressure limit | Csg07 | Setpoint of analog valve
DBD32 | Real | sParR8 | Real - Dialogue | PT08 | Pressure limit | Csg08 | Setpoint of analog valve
DBD36 | Real | sParR9 | Real - Dialogue | PT09 | Pressure limit | Csg09 | Setpoint of analog valve
|  |  |  | PT010 | Pressure limit | Csg010 | Setpoint of analog valve
|  |  |  | PT011 | Pressure limit | Csg011 | Setpoint of analog valve
|  |  |  | PT012 | Pressure limit | Csg012 | Setpoint of analog valve

## Alarm
Bool Alarm
PLC -> Epics
Type "Plc_to_Epi_Alarm"
DBX0.0 | Bool | Al1 | Alarm | F_pilz | Fault on emergency stop
DBX0.1 | Bool | Al2 | Alarm | F_J000 | Fault on Vaccum pumping system J000 | No connected to the PLC
DBX0.2 | Bool | Al3 | Alarm | F_J001 | Fault on Vaccum pumping system J001 | No connected to the PLC
DBX0.3 | Bool | Al4 | Alarm | F_P000 | Fault on Vaccum pump P000 | No connected to the PLC
DBX0.4 | Bool | Al5 | Alarm | F_SH300 | Fault on supercritical helium production | No connected to the PLC
DBX0.5 | Bool | Al6 | Alarm | MKS1.Fault/Send | Fault on data Send
DBX0.6 | Bool | Al7 | Alarm | MKS1.Fault/Recv | Fault on data Receive
DBX0.7 | Bool | Al8 | Alarm | MKS1.Fault/Local_mode | Fault Local mode
DBX1.0 | Bool | Al9 | Alarm | MKS1.Fault/Learning | Fault Learning
DBX1.1 | Bool | Al10 | Alarm | MKS1.Fault/SP_Control | Fault on Setpoint Control
DBX1.2 | Bool | Al11 | Alarm | MKS1.Fault/Wr_SP_Type0 | Fault on Writing of Type0 Setpoint
DBX1.3 | Bool | Al12 | Alarm | MKS1.Fault/Wr_SP_Type1 | Fault on Writing of Type1 Setpoint
DBX1.4 | Bool | Al13 | Alarm | MKS1.Fault/Wr_SP | Fault on Setpoint writing
DBX1.5 | Bool | Al14 | Alarm | MKS1.Fault/Wr_SP_Sel | Fault on setpoint selection writing
DBX1.6 | Bool | Al15 | Alarm | MKS1.Fault/Wr_Kp | Fault on Kp writing
DBX1.7 | Bool | Al16 | Alarm | MKS1.Fault/Wr_Ti | Fault on Ti writing
DBX2.0 | Bool | Al17 | Alarm | MKS1.Fault/Wr_Out_Val | Fault on Out_Val writing
DBX2.1 | Bool | Al18 | Alarm | MKS1.Fault/Wr_PT01 | Fault on PT01 Writing
DBX2.2 | Bool | Al19 | Alarm | MKS1.Fault/Wr_Status | Fault on Status wrinting
DBX2.3 | Bool | Al20 | Alarm | MKS1.Fault/Verif_SP_Type0 | Fault on Setpoint Type0 checking
DBX2.4 | Bool | Al21 | Alarm | MKS1.Fault/Verif_SP_Type1 | Fault on Setpoint Type1 checking
DBX2.5 | Bool | Al22 | Alarm | MKS1.Fault/Verif_SP | Fault on Setpoint checking
DBX2.6 | Bool | Al23 | Alarm | MKS1.Fault/Verif_SP_Sel | Fault on Setpoint Selection checking
DBX2.7 | Bool | Al24 | Alarm | MKS1.Fault/Verif_Kp | Fault on Kp checking
DBX3.0 | Bool | Al25 | Alarm | MKS1.Fault/Verif_Ti | Fault on Ti checking
DBX3.1 | Bool | Al26 | Alarm | MKS1.Fault/Verif_Out_Val | Fault on Out_Val checking
DBX3.2 | Bool | Al27 | Alarm | MKS1.Fault/Verif_PT01 | Fault on PT01 checking
DBX3.3 | Bool | Al28 | Alarm | MKS1.Fault/Verif_Status | Fault on Status checking
DBX3.4 | Bool | Al29 | Alarm | MKS2.Fault/Send | Fault on data Send
DBX3.5 | Bool | Al30 | Alarm | MKS2.Fault/Recv | Fault on data Receive
DBX3.6 | Bool | Al31 | Alarm | MKS2.Fault/Local_mode | Fault Local mode
DBX3.7 | Bool | Al32 | Alarm | MKS2.Fault/Learning | Fault Learning
DBX4.0 | Bool | Al33 | Alarm | MKS2.Fault/SP_Control | Fault on Setpoint Control
DBX4.1 | Bool | Al34 | Alarm | MKS2.Fault/Wr_SP_Type0 | Fault on Writing of Type0 Setpoint
DBX4.2 | Bool | Al35 | Alarm | MKS2.Fault/Wr_SP_Type1 | Fault on Writing of Type1 Setpoint
DBX4.3 | Bool | Al36 | Alarm | MKS2.Fault/Wr_SP | Fault on Setpoint writing
DBX4.4 | Bool | Al37 | Alarm | MKS2.Fault/Wr_SP_Sel | Fault on setpoint selection writing
DBX4.5 | Bool | Al38 | Alarm | MKS2.Fault/Wr_Kp | Fault on Kp writing
DBX4.6 | Bool | Al39 | Alarm | MKS2.Fault/Wr_Ti | Fault on Ti writing
DBX4.7 | Bool | Al40 | Alarm | MKS2.Fault/Wr_Out_Val | Fault on Out_Val writing
DBX5.0 | Bool | Al41 | Alarm | MKS2.Fault/Wr_PT01 | Fault on PT01 Writing
DBX5.1 | Bool | Al42 | Alarm | MKS2.Fault/Wr_Status | Fault on Status wrinting
DBX5.2 | Bool | Al43 | Alarm | MKS2.Fault/Verif_SP_Type0 | Fault on Setpoint Type0 checking
DBX5.3 | Bool | Al44 | Alarm | MKS2.Fault/Verif_SP_Type1 | Fault on Setpoint Type1 checking
DBX5.4 | Bool | Al45 | Alarm | MKS2.Fault/Verif_SP | Fault on Setpoint checking
DBX5.5 | Bool | Al46 | Alarm | MKS2.Fault/Verif_SP_Sel | Fault on Setpoint Selection checking
DBX5.6 | Bool | Al47 | Alarm | MKS2.Fault/Verif_Kp | Fault on Kp checking
DBX5.7 | Bool | Al48 | Alarm | MKS2.Fault/Verif_Ti | Fault on Ti checking
DBX6.0 | Bool | Al49 | Alarm | MKS2.Fault/Verif_Out_Val | Fault on Out_Val checking
DBX6.1 | Bool | Al50 | Alarm | MKS2.Fault/Verif_PT01 | Fault on PT01 checking
DBX6.2 | Bool | Al51 | Alarm | MKS2.Fault/Verif_Status | Fault on Status checking
DBX6.3 | Bool | Al52 | Alarm | MKS3.Fault/Send | Fault on data Send
DBX6.4 | Bool | Al53 | Alarm | MKS3.Fault/Recv | Fault on data Receive
DBX6.5 | Bool | Al54 | Alarm | MKS3.Fault/Local_mode | Fault Local mode
DBX6.6 | Bool | Al55 | Alarm | MKS3.Fault/Learning | Fault Learning
DBX6.7 | Bool | Al56 | Alarm | MKS3.Fault/SP_Control | Fault on Setpoint Control
DBX7.0 | Bool | Al57 | Alarm | MKS3.Fault/Wr_SP_Type0 | Fault on Writing of Type0 Setpoint
DBX7.1 | Bool | Al58 | Alarm | MKS3.Fault/Wr_SP_Type1 | Fault on Writing of Type1 Setpoint
DBX7.2 | Bool | Al59 | Alarm | MKS3.Fault/Wr_SP | Fault on Setpoint writing
DBX7.3 | Bool | Al60 | Alarm | MKS3.Fault/Wr_SP_Sel | Fault on setpoint selection writing
DBX7.4 | Bool | Al61 | Alarm | MKS3.Fault/Wr_Kp | Fault on Kp writing
DBX7.5 | Bool | Al62 | Alarm | MKS3.Fault/Wr_Ti | Fault on Ti writing
DBX7.6 | Bool | Al63 | Alarm | MKS3.Fault/Wr_Out_Val | Fault on Out_Val writing
DBX7.7 | Bool | Al64 | Alarm | MKS3.Fault/Wr_PT01 | Fault on PT01 Writing
DBX8.0 | Bool | Al65 | Alarm | MKS3.Fault/Wr_Status | Fault on Status wrinting
DBX8.1 | Bool | Al66 | Alarm | MKS3.Fault/Verif_SP_Type0 | Fault on Setpoint Type0 checking
DBX8.2 | Bool | Al67 | Alarm | MKS3.Fault/Verif_SP_Type1 | Fault on Setpoint Type1 checking
DBX8.3 | Bool | Al68 | Alarm | MKS3.Fault/Verif_SP | Fault on Setpoint checking
DBX8.4 | Bool | Al69 | Alarm | MKS3.Fault/Verif_SP_Sel | Fault on Setpoint Selection checking
DBX8.5 | Bool | Al70 | Alarm | MKS3.Fault/Verif_Kp | Fault on Kp checking
DBX8.6 | Bool | Al71 | Alarm | MKS3.Fault/Verif_Ti | Fault on Ti checking
DBX8.7 | Bool | Al72 | Alarm | MKS3.Fault/Verif_Out_Val | Fault on Out_Val checking
DBX9.0 | Bool | Al73 | Alarm | MKS3.Fault/Verif_PT01 | Fault on PT01 checking
DBX9.1 | Bool | Al74 | Alarm | MKS3.Fault/Verif_Status | Fault on Status checking
DBX9.2 | Bool | Al75 | Alarm | Linde_LHe_LI_OK | Lhe level in the dewar ok
DBX9.3 | Bool | Al76 | Alarm | CV5202_Intrlck | Allow to open the valve
DBX9.4 | Bool | Al77 | Alarm
DBX9.5 | Bool | Al78 | Alarm
DBX9.6 | Bool | Al79 | Alarm
DBX9.7 | Bool | Al80 | Alarm