## E-S PDG
13P091-01-3220-01-305
305 | 2025-02-04 | Updated SQ7, SQ8 |  | KG
304 | 2025-01-27 | Updated SQ9 |  | KG
302 | 2015-06-27 | Update after starting |  | AJO
301 | 2015-05-13 | Update for new vlaves FV550 to FV558 |  | AJO
300 | 2014-10-29 | Update after Uppsala Commitionning |  | AJO
207 | 2014-08-27 | Update after ACS Tests |  | AJO
206 | 2014-08-25 | Update for ACS Tests |  | AJO
205 | 2014-08-05 | Update after Lery Commissioning |  | BOK | AJO
204 | 2014-07-10 | For Commission at Cryodiffusion |  | BOK | AJO
VERSION | DATE |  | MODIFICATION | Dess. Par | Vérifié par | App. Par
[5 empty] | Date : | 2025-02-04
[5 empty] | Page : 0 | Rév. : 305
CRYO DIFFUSION
49, rue Verdun 27690 LERY
CONTROLE CRYOSTAT UPPSALA
Grafcets

## Sommaire (hidden)
SOMMAIRE
Date | Indice | Nom du GRAFCET |  | Commentaire
|  |  | 001 |  | Cond_pasto2 | Grafcet conduite pasto 22
|  |  | 001 |  | G7_Cond_pasto | Conditionneuse pasto 22
|  |  | 001 |  | G7_dem_pasto | Grafcet démarrage past 22
|  |  | 001 |  | G7_prepa_d_pasto | grafcet de préparation des solutions de débourrage
|  |  | 001 |  | G7_debour_pasto | Grafcet du débourrage et de sa distribution
|  |  | 001 |  | G7_prod_pasto | Grafcet de production pasto 22
|  |  | 001 |  | G7_homo_pasto | Grafcet homo pasto 22
|  |  | 001 |  | G7_pousse_t1 | Grafcet de pousse trémie 1
|  |  | 001 |  | G7_pousse_fr2 | Grafcet de pousse poste fruit 2 (fruit en mélange)
|  |  | 001 |  | G7_POUSSE_AR1
|  |  | 001 |  | G01 | T01 Dosage d'eau
|  |  | 001 |  | G02 | T01 Into
|  |  | 001 |  | F04 | T01 Refroidissement ON
|  |  | 001 |  | F07 | T01 Introduction MP par dôme

## GXX (hidden)
GXX : TITRE
Mot G7
Mot timer
Bit étape
SR Gestion
SR Action
Aide-memoire:
: %MW
: %MW
: %M
: 10
: 100

## G7_Seq0
FC n°200
DB n°200
He conditioning stop
[7 empty] | He conditioning start | [9 empty] | He conditioning start
[7 empty] | & Cycle Number > 0 | [9 empty] | & Cycle Number <= 0
Stop
[8 empty] | Check parameters | [5 empty] | FV011 closed
Valid or all parameter > 0
[8 empty] | Check equipment |  |  |  |  | FV011 closed
Valid ou Equipment OK
[8 empty] | Preliminary |  |  | Run P000,
[8 empty] | drain |  |  | FV010 & FV502 open; FV011 closed
|  | PT500 >= 5 mbar |  |  |  |  | PT500 < Low Vacuum (5 mbar)
& Alarm Vacuum timer
| X12 | [6 empty] | Time out of |  |  |  | FV011 closed
Vacuum timer
|  |  | PT500 > High Vacuum (10 mbar) | [10 empty] | PT500 < High Vacuum (10 mbar)
[7 empty] | FV011 closed | [7 empty] | GHe filling |  |  | FV012 & FV502 opened
FV011 closed
|  |  | Alarm | [10 empty] | PT500 > High Filling (1080 mbar)
|  |  | confirmed |  |  | PT500 <= High Filling
& Alarm Pressure timer
[15 empty] | Time out of |  |  | FV011 closed
[5 empty] | X14 | [9 empty] | Pressure timer
|  |  | PT500 < Low Filling | [6 empty] | PT500 > Low Filling (1020 mbar) | [8 empty] | PT500 > Low Filling
[10 empty] | & Current cycle >= N° of cycle | [8 empty] | & Current cycle < N° of cycle
|  |  |  | Pressure alarm |  |  | FV011
closed
Alarm confirmed
[5 empty] | 13P091-01-3220-01-305 | [12 empty] | 2025-02-04
PAGE 2
SQ0 : Transfer Line L000 and Purging System, Conditioning He Circuits
4
12
Vaccum alarm
6
8
0
10
14
2
Aide-memoire:
1

## G7_Seq1
FC n°201
DB n°201
He conditioning stop
[8 empty] | He conditioning start | [9 empty] | He conditioning start
[8 empty] | & Cycle Number > 0 | [9 empty] | & Cycle Number <= 0
Stop
[9 empty] | Check parameters | [5 empty] | FV011 closed
Valid or all parameter > 0
[9 empty] | Check equipment |  |  |  |  | FV011 closed
Valid or Equipment OK
[9 empty] | Preliminary |  |  | Run P000 | [6 empty] | FV101,CV100,CV101,CV102,
[9 empty] | drain |  |  | FV010 & FV100 | [6 empty] | CV103,CV104,CV105,CV550,
CV551, CV552 opened
FV011 closed
|  | MKS1 >= 5 mbar | [5 empty] | MKS1 < Low Vacuum (5 mbar)
& Alarm Vacuum timer
FV101,CV100,CV101,CV102,
| X12 | [7 empty] | Time out of |  |  |  | CV103,CV104,CV105,CV550,
[9 empty] | Vacuum timer |  |  |  | CV551 open; FV011 closed
|  |  | MKS1 > High Vacuum (10 mbar) | [11 empty] | MKS1 < High Vacuum (10 mbar)
[8 empty] | FV011 closed | [7 empty] | GHe filling |  |  | FV012 & FV100 open
FV011 closed
FV101,CV100,CV101,CV102,
|  |  | Alarm | [11 empty] | MKS1 > High Filling (1080 mbar)
|  |  | confirmed |  |  |  | MKS1 <= High Filling
[7 empty] | & Alarm Pressure timer | [11 empty] | FV101,CV100,CV101,CV102,
[16 empty] | Time out of |  |  | CV103,CV104,CV105,CV550,
[5 empty] | X14 | [10 empty] | Pressure timer |  |  | CV551 open; FV011 closed
|  |  | MKS1 < Low Filling | [7 empty] | MKS1 > Low Filling (1020 mbar) | [8 empty] | MKS1 > Low Filling
[11 empty] | & Current cycle >= N° of cycle | [8 empty] | & Current cycle < N° of cycle
|  |  |  | Pressure alarm |  |  |  | FV011
closed
Alarm confirmed
[6 empty] | 13P091-01-3220-01-305 | [12 empty] | 2025-02-04
PAGE 3
SQ1 : Cryostat, conditioning He Circuit
4
12
Vaccum alarm
6
8
0
10
14
2
Aide-memoire:
1

## G7_Seq2
FC n°202
DB n°202
He conditioning stop
[7 empty] | He conditioning start | [9 empty] | He conditioning start
[7 empty] | & Cycle Number > 0 | [9 empty] | & Cycle Number <= 0
Stop
[8 empty] | Check parameters | [5 empty] | FV011 closed
Valid or all parameter > 0
[8 empty] | Check equipment |  |  |  |  | F>V011 closed
Valid ou Equipment OK
[8 empty] | Preliminary |  |  | Run P000 | [6 empty] | CV301,CV302 opened
[8 empty] | drain |  |  | FV010 & FV300 opened | [6 empty] | FV011 closed
PT301 & 302>= 5 mbar
|  | & Alarm Vacuum timer |  |  |  |  | PT301 & PT302 < Low Vacuum (5 mbar)
X12
[8 empty] | Time out of |  |  |  | CV301,CV302 opened
[8 empty] | Vacuum timer |  |  |  | F>V011 closed
|  |  | PT301 OR PT302 | [10 empty] | PT301 & PT302 < High Vacuum (10 mbar)
> High Vacuum (10 mbar)
[7 empty] | FV011 closed | [7 empty] | GHe filling |  | FV012 & FV300 opened
CV301,CV302 open; FV011 closed
|  |  | Alarm |  |  | PT301 OR PT302 | [7 empty] | PT301 & PT302 > High Filling (1080 mbar)
|  |  | confirmed |  |  | <= High Filling
& Alarm Pressure timer
[15 empty] | Time out of |  |  | CV301,CV302 opened
[5 empty] | X14 | [9 empty] | Pressure timer |  |  | FV011 closed
|  |  | PT301 & PT302 | [6 empty] | PT301 & PT302 > Low Filling | [8 empty] | PT301 & PT302 > Low Filling
|  |  | < Low Filling (1020 mbar) | [6 empty] | & Current cycle >= N° of cycle | [8 empty] | & Current cycle < N° of cycle
|  |  |  | Pressure alarm |  |  | FV011
closed
Alarm confirmed
[5 empty] | 13P091-01-3220-01-305 | [12 empty] | 2025-02-04
PAGE 4
SQ2 : Couplers, conditioning ScHe Circuits
4
12
Vaccum alarm
6
8
0
10
14
2
Aide-memoire:
1

## G7_Seq3A
FC n°203 | [5 empty] | LN2 flow stop
DB n°203
ICB, thermal shield cooling
Check parameters
Valid or all parameter > 0
Check equipment
Valid ou Equipment OK
[6 empty] | LN2 flow |  |  | LN2 flow request
(up to Linde)
EV400 opened
TT403 Or TT400 < Cool down Tt (200 K)
[6 empty] | LN2 flow |  |  | EV400 opened | Heater EH400
TT401B Or TT400 < Low Tt cooling (85 K)
LN2 flow stop
TT401B And TT400 > High Tt cooling (100 K)
LN2 flow in ICB stop
EH400
|  | Gas heating | EH400 running
TT400 > EH400 High limit (30 °C)
|  | Heating stop | EH400 stopped
TT400 < EH400 Low Limit (10 °C)
|  |  |  | 13P091-01-3220-01-305 | [6 empty] | 2025-02-04
PAGE 5
SQ3A : ICB - THERMAL SHIELD COOLING
4
A
6
0
B
8
2
Aide-memoire:
1

## G7_Seq3B
FC n°204
DB n°204
|  |  | LN2 flow stop |  |  |  |  | FV400 closed
Run . SQ5
Cryostat, LN2 flow start
Check parameters
Valid or all parameter > 0
Check equipment
Valid ou Equipment OK
|  |  | LN2 flow |  |  | FV400 opened
TT403 < Cool down Tt (100 K)
|  |  | LN2 flow |  |  | EH200 & |  |  | EV201 opened |  |  |  | EV200 opened
[9 empty] | TT216B & TT206 > High Tt cooling (100k) |  |  |  | TT214B & TT205 > High Tt cooling (100k)
|  |  | LN2 flow stop |  |  | EH 201 |  |  | EV201 closed |  |  |  | EV200 closed
[9 empty] | TT216B Or TT206 < Low Tt cooling (85k) |  |  |  | TT214B Or TT205 < Low Tt cooling (85k)
FV400 opened
LN2 flow stop
[10 empty] | EH 200 |  |  |  |  | EH201
|  | Gas heating |  |  | EH200 running | [6 empty] | Gas heating |  | EH201 running
|  | start | [9 empty] | start
| TT205 > High Limit (30 °C) | [9 empty] | TT206 > High Limit (30 °C)
|  | Gas heating |  |  | EH200 stopped | [6 empty] | Gas heating |  | EH201 stopped
|  | stop | [9 empty] | stop
| TT205 < Low Limit (10 °C) | [9 empty] | TT206 < Low Limit (10 °C)
[7 empty] | 13P091-01-3220-01-305 | [6 empty] | 2025-02-04
PAGE 6
SQ3B : CRYOSTAT - THERMAL SHIELD COOLING
Aide-memoire:
4
A
6
0
B
C
D
2
1

## G7_Seq4
FC n°205
DB n°205
LN2 flow stop
Run . SQ5
Cryostat, LN2 flow start
Check parameters
Valid or all parameter > 0
Check equipment
Valid ou Equipment OK
Coupleur 1 ou Coupleur 2
[8 empty] | Coupleur 1 |  |  |  | Coupleur 2
[5 empty] | LN2 flow |  | Regulation CV200 |  |  | Regulation CV201 |  |  |  |  | EH 202
[7 empty] | TT208 & TIC200 or |  |  | TT210 & TIC201 or |  |  |  |  | EH203
[7 empty] | FT200 & FIC200 |  |  | FT201& FIC201 |  |  |  |  | FV200
Stopping
| Coupleur 1 | [7 empty] | Coupleur 2
[8 empty] | EH202 | [7 empty] | EH203
|  |  | Gas heating | EH202 running | [6 empty] | Gas heating |  |  | EH203 running
|  |  | start | [7 empty] | start
|  | TT211 > High Limit (30 °C) | [7 empty] | TT212 > High Limit (30 °C)
|  |  | Gas heating | EH202 stopped | [6 empty] | Gas heating |  |  | EH203 stopped
|  |  | stop | [7 empty] | stop
|  | TT211 < Low Limit (10 °C) | [7 empty] | TT212 < Low Limit (10 °C)
[5 empty] | 13P091-01-3220-01-305 | [7 empty] | 2025-02-04
PAGE 7
SQ4 : TESLA COUPLERS COOLING
6
0
2
A
B
C
D
Aide-memoire:
4
1

## G7_Seq5
FC n°206
DB n°206
Start
Check parameters
Valid or all parameter > 0
Check equipment
Valid ou Equipment OK
LHe 4K
Degassing
4 K vessel order & LT100 < Low Level
Memo TT101 > 50 K
|  |  | Cool down | FV500, |  | CV100 opened
|  |  | TL L001 | CV550 opened |  | FV101 opened
Not Memo TT101 > 50 K
TT100 < Filling Tt
|  |  | Start of 4K vessel | CV100 opened & controlled |  |  |  | FV500,CV550 opened
|  |  | filling |  | PT100>Warning Pressure |  |  | FV101 closed
FT550<Warning Flow
LT100 > High Level
|  |  | Stop of 4K vessel | FV101 opened
|  |  | filling | CV550 opened
| LT100 < Low Level |  |  |  | Stop of 4k vessel filling sequence
|  | 13P091-01-3220-01-305 | [5 empty] | 2025-02-04
PAGE 8
SQ5 : CONTROL LEVEL 4 K VESSEL
Aide-memoire:
6
0
8
10
2
4
1

## G7_Seq6
FC n°207
DB n°207
Lhe level measurement
Run . SQ5
SQ5,Activate
Check parameters
Valid or all parameter > 0
Check equipment
Valid ou Equipment OK
Contrôle Level measurement
Stop
|  | Temperature |  | No level |  | Temperature
|  | control |  | measurement |  | control |  | measurement
| TT101 < Security Tt (20 K) |  |  |  | TT113 < Security (20 K)
|  | LT100 measure |  |  |  | LT101 measure
| TT101 > Security Tt (20 K) |  |  |  | TT113 > Security Tt (20 K)
| & LT100 < Security Lt (5%) |  |  |  | & LT101 < Security Lt (5%)
|  |  | 13P091-01-3220-01-305 |  |  |  | 2025-02-04
PAGE 9
SQ6 : LHe level measurement
Aide-memoire:
A
0
B
C
D
4
2
1

## G7_Seq7
FC n°208
DB n°208
Start
Check parameters
Valid or all parameter > 0
Check equipment
(Valid ou Equipment OK) & SQ5
CV550,
CV551,CV552 opened
|  | Cavity 1 ou Cavity2 ou Table ou Shield |  |  |  |  | Table
|  |  | Coupleur 1 |  | Coupleur 2 |  |  |  | Shield
|  | Cooling Cavity 1 |  | Cooling Cavity 2 |  | Table | Ecran |  | CV550,
CV551,CV552 opened
Stop OR (AutomaticStartSQ8 & SQ8 is running & step > 2)
| 13P091-01-3220-01-305 | [6 empty] | 2025-02-04
PAGE 10
SQ7 : Cryostat, Cool Down He Circuits
Aide-memoire:
1 : Cavity 1 = P_C1
2 : Cavity 2 = P_C2
3 : Table = P_Tbl
4 : Ecran = P_MS ( Magnetic Shield)
5 : AutoStartSQ8 = P_AutoStartSQ8
6
0
2
4
1

## SQ7
FC n°208
DB n°208
FC n°208
DB n°208
| Cavity 1 |  |  |  | CV102 opened and controlled | [5 empty] | Cavity 2 |  |  | CV103 opened and controlled
| cooling |  |  |  | PT100 < reference P & | [5 empty] | cooling |  |  | PT100 < reference P &
[5 empty] | FT552 < reference FT | [8 empty] | FT552 < reference FT
LT101 > 2K High Level
[7 empty] | Stop of cavity |  |  |  | CV102,CV103 closed
[7 empty] | filling |  |  |  | CV104 closed
LT101 < 2K Low Level
[7 empty] | Maintain LHe level |  |  |  | CV104 opened and controlled
PT100 < reference P &
FT552 < reference FT
LT101 > 2K High Level
Table or magnetic shield
[7 empty] | Cooling | CV101 opened and controlled
[7 empty] | table | PT100 < reference P &
FT550 < reference FT
|  | TT107 < TT Equip Cooling & no thermal shield | [6 empty] | TT107 < TT Equip Cooling & thermal shield
|  |  | Keeping | Regulation CV101 | [5 empty] | Magnetic |  |  | CV101 opened and controlled
|  |  | cold | TT107 = reference T° | [5 empty] | shield |  |  | PT100 < reference P &
|  |  |  | PT100 < reference P | [5 empty] | cooling |  |  | FT550 < reference FT
TT126 < TT Equip Cooling
[10 empty] | Keeping |  | Regulation CV101
[10 empty] | cold |  | TT128 = reference T°
PT100 < reference P
[5 empty] | 13P091-01-3220-01-305 | [7 empty] | 2025-02-04
PAGE 11
SQ7 : CRYOSTAT, COOL DOWN He CIRCUITS
Aide-memoire:
1 :Reference P = P_Pt
2 :Reference FT = P_FT550
3 :Reference T° = P_SP_Tt
4 :Reference LT = P_HighLt
5 :LTmin = P_LowLt
6 : 6K = P_Tt_Cold
7 :Thermal shiel & Magnectic shield = P_MS
8 : Table = P_Tbl
9
11
10
12
7
8
5
6
A
B

## G7_Seq8
FC n°209
DB n°209
|  | 4K operation | [5 empty] | FV500 fermée
|  | stop in charge | [5 empty] | CV100, CV101, CV102, CV103, CV104, CV105 fermés
FV101, CV550, CV551, CV552 ouvertes
SQ7.Activate Or SQ9.Activate Or SQ11.Activate Or SQ13.Activate Or 4 K operation order
4K operation
stop
4 K operation order OR (SQ7 running & AutoStartSQ8 & keeping cold selected equipment & 2K status ON)
Check parameters (CV551 can be 0)
Valid or parameter > 0
Check equipment
Valid or Equipment OK
|  | 4K vessel |  |  |  |  | CV550,CV552 opened
conditioning
| Table ou magnetic shield | [8 empty] | Table & /Shield |  | Shield
|  | Keeping |  |  | Regulation CV101 | [5 empty] | Regulation CV101
|  | cold |  |  | TT107 = reference T° | [5 empty] | TT128 = reference T° |  |  | SQ5 | 2K
CV550,CV552 opened
| 4 K operation stop | [10 empty] | CV551
2K
LT101 < LT min
|  |  |  | Start of |  |  |  | CV104 opened and controlled
|  |  |  | 2 K vessel |  |  |  | PT101 < Warning pressure
filling
LT101 > High Level
|  |  |  | Stop of |  |  |  |  | CV104 closed
2 K vessel
filling
LT101 < Low Level
[6 empty] | 13P091-01-3220-01-305 | [7 empty] | 2025-02-04
PAGE 13
SQ 8 : 4 K OPERATION
0
6
4
A
B
2
Aide-memoire:
1
20

## G7_Seq9
FC n°210 | [23 empty] | 2025-01-27
DB n°210
|  | 4K operation |  |  |  |  | FV500 closed
|  | stop in charge |  |  |  |  | CV100, CV101, CV102, CV103, CV104, CV105 closed
FV101, FV552, CV550, CV551, CV552 open
SQ7.Activate OR SQ8.Activate OR SQ11.Activate OR SQ13.Activate OR CM 2K operation order
2 K
stop
2 K operation order
|  | Check parameters |  |  |  |  | Open : |  | CV552 |  |  | FV552
Valid OR all parameter > 0
|  |  |  | Check equipment |  |  |  | Open : |  | CV552 |  |  | FV552
Valid OR Equipment OK
Switch 2K to Keaser Mode
Keaser mode
|  | 2K Pumps Ready | [7 empty] | Open : |  |  | CV552 |  |  | FV552
[13 empty] | FV551 |  |  | FV555 |  |  | FV557
Valid (sent by the sequencer program when enabled automatic control of 2K pumps)
|  | Close CV552 | [7 empty] | Open : |  |  | FV551 |  |  | FV555 |  |  | FV557
FV552 5sec later
Tps >= 10s
|  | 2 K |  |  | CV550 opened | [6 empty] | Open : |  |  | FV551
|  | operation |  |  | 2K pumps running | [9 empty] | FV555
|  | start |  |  | CV551 external control | [9 empty] | FV557
Table OR magnetic shield
[7 empty] | Table | [6 empty] | Magnetic Shield
|  | Keeping |  | Regulation CV101 | [5 empty] | Regulation CV101 | [12 empty] | Open : |  | FV551
|  | cold |  | TT107 = reference T° | [5 empty] | TT128 = reference T° | [8 empty] | SQ5 |  | 2K |  |  |  | FV555
|  |  |  | CV550 opened | [20 empty] | FV557
He pumps start
CV551 external control
Stopping
|  | Pressure |  |  | Stopped 2K pumps | [9 empty] | Open : |  |  | FV551
|  | rise |  |  | Close CV551 | [12 empty] | FV555
FV557
PT101 > Final Pressure (1000 mbar)
|  | Open CV552 | [7 empty] | Open : |  |  | FV551 |  |  | FV557
|  | FV552 5sec before | [10 empty] | FV555
Tps >= 10s
|  | Pumping System Stopped (0 rpm) | [8 empty] | Open : |  |  | CV552 |  |  | FV552
[14 empty] | FV551 |  |  | FV555 |  |  | FV557
Pumping Syst freq=0 OR Valid when frequency can't be read
|  | Pumping System Venting | [8 empty] | Open : |  |  | CV552 |  |  | FV552
[14 empty] | FV551 |  |  | FV556 |  |  | FV557
2KPumps:PT552 > 990 mbar OR Valid when Pressure can't be read
[5 empty] | LT101 < LT min | [16 empty] | 2K
[6 empty] | Start of |  |  | CV105 opened and controlled
[6 empty] | 2 K vessel |  |  | PT101 or |  |  |  | PT102 < Warning Pressure
filling
LT101 > High Level
[6 empty] | Stop of |  |  |  | CV105 closed
2 K vessel
filling
LT101 < Low Level
|  |  | 13P091-01-3220-01-305 | [16 empty] | 2025-02-04
PAGE 14
SQ9 : 2 K OPERATION
A
B
0
12
10
2
14
1
30
4
6
8
16
18
20
Aide-memoire:

## G7_Seq10
FC n°211
DB n°211
[5 empty] | SHe operation stop |  |  | Compressor stopped
Start
Check parameters
Valid or all parameter > 0
Check equipment
Valid ou Equipment OK
[5 empty] | Check Coupler |  |  | Start Compressor
Coupleur 1 Or Coupleur 2
[6 empty] | Coupleur 1 |  |  |  | Coupleur 2
[5 empty] | Regulation CV301 |  |  | Regulation CV302 |  |  | EH301
[5 empty] | TT303 = reference T° or |  |  | TT304 = reference T° or
[5 empty] | FT301 = reference FT |  |  | FT302 = reference FT |  |  | EH302
[5 empty] | FV301 opened |  |  | FV302 opened
Stopping
[7 empty] | EH301 |  |  |  |  | EH302
|  | Gas heating | EH301 running | [6 empty] | Gas heating | EH302 running
|  | start | [7 empty] | start
| TT307 > High Limit (30 °C) | [7 empty] | TT308 > High Limit (30 °C)
|  | Gas heating | EH301 stopped | [6 empty] | Gas heating | EH302 stopped
|  | stop | [7 empty] | stop
| TT307 < Low Limit (10 °C) | [7 empty] | TT308 < Low Limit (10 °C)
|  |  |  | 13P091-01-3220-01-305 | [6 empty] | 2025-02-04
PAGE 15
SQ10 : SUPERCRITICAL CIRCUITS OPERATION
Aide-memoire:
A
B
C
D
0
6
4
2
1

## G7_Seq11
FC n°212
DB n°212
Standby
|  | operation |  |  |  | Run . SQ5
stopped
Standby 4 K operation start
Check parameters
Valid or all parameter > 0
Check equipment
Valid ou Equipment OK
|  | Conditioning |  |  |  | CV550,CV552 opened
CV105 closed
Table And Not Magnetic shield ou Magnetic shield
[5 empty] | Table |  |  |  |  | Magnetic shield
|  | Keeping |  | Regulation CV101 |  |  |  |  | Regulation CV101 |  | LHe Flow
|  | cold |  | TT107 = reference T° |  |  |  |  | TT128 = reference T°
CV550,CV552 opened
| Stanby 40 K operation stop | [7 empty] | CV105 closed
LHe Flow
(Cavity 1 And TT125 > Lhe flow Tt)
OR (Cavity 2 And TT126 > Lhe flow Tt)
|  |  | LHe flow |  |  |  | CV102 & CV103 opened and controlled
|  |  | start |  |  |  | PT101 < Warning Pressure
(TT125 < Lhe flow Tt OR NOT Cavity 1)
AND (TT126 < Lhe flow Tt OR NOT Cavity 2)
|  |  | LHe flow |  |  |  |  | CV102 & CV103 closed
stop
(Cavity 1 And TT125 > Lhe flow Tt)
OR (Cavity 2 And TT126 > Lhe flow Tt)
[5 empty] | 13P091-01-3220-01-305 | [6 empty] | 2025-02-04
PAGE 16
SQ11 : STANDBY 40 K
Aide-memoire:
A
B
0
6
4
2
1

## G7_Seq12A
FC n°213
DB n°213
Warm-up stop
Warm-up ICB
Check parameters
Valid or all parameter > 0
Check equipment
Valid ou Equipment OK
EH401
TT402 > Warm-up Tt (20°C)
Warm-up end
Fin_Warm-Up
EH401
|  | Thermal shield | EH401 RUN
warm-up start
TT401 > High Limit (20 °C)
|  | Thermal shield | EH401 STOP
warm-up stop
TT401 < Low Limit (0 °C)
|  |  |  | 13P091-01-3220-01-305 |  |  | 2025-02-04
PAGE 17
SQ12A : WARM-UP ICB
Aide-memoire:
A
B
0
6
4
2
1

## G7_Seq12B
FC n°214
DB n°214
Warm-up stop
Warm-up ICB
Check parameters
Valid or all parameter > 0
Check equipment
Valid ou Equipment OK
CV550,CV551,CV552,FV101,CV100 à CV105,
FV200,EV200,EV201,CV200,CV201,FV301,CV302, FV302, CV301
opened
EH100 EH101 EH102 EH103 EH104 EH105 EH106 EH204 EH205
EH206 EH207 EH208 EH300 EH107 EH108
Thermometers > Warm-up Tt (20°C)
Warm-up end
Fin_Warm-Up
| 13P091-01-3220-01-305 |  |  | 2025-02-04
PAGE 18
SQ12B : WARM-UP CRYOSTAT
Aide-memoire:
0
4
2
6
1

## G7_Seq13
FC n°215
DB n°215
Start Cryostat isolation
Check parameters
Valid or all parameter > 0
Check equipment
Valid ou Equipment OK
Pressure Control
|  |  |  | PT300 ou PT301 ou PT302 > She Alarm (6 bars) | [7 empty] | PT100 | [6 empty] | Not Cryostat isolation
ou PT101 > He Alarm (1300 mbar)
[5 empty] | Pressure Alarm SHe circuit | [7 empty] | Pressure Alarm He circuit | [6 empty] | Helium recovry
[5 empty] | Ouverture CV550, | [7 empty] | Ouverture CV550, | [6 empty] | Ouverture CV550,
[5 empty] | CV551, CV552 | [7 empty] | CV551, CV552 | [6 empty] | CV551, CV552
|  |  |  | A |  |  | B |  |  | C |  | A |  |  | B |  | C |  | A |  |  | B
|  | 0 |  |  |  | 4 |  | 10 |  |  | 0 |  |  | 4 |  | 10 |  | 0 |  |  | 4
A = Sequence Stopping
B = Not Alarm & Cryostat isolation
C = Not Alarm & Not Cryostat isolation
Not Alarm :
X6 = PT300 & PT301 & PT302 < She Pressure (5 bars)
X8 = PT100 & PT101 < He Pressure (1050 mbar)
[9 empty] | 13P091-01-3220-01-305 | [8 empty] | 2025-02-04
PAGE 19
SQ13 : CRYOSTAT ISOLATED
Aide-memoire:
1 : Cryostat isolation = P_Isol_cryo
2 : 5 bar = P_SHe
3 : 6 bar = P_Al_SHe
4 : 1050 mbar = P_He
5 : 1300 mbar = P_Al_He
0
4
2
1
6
8
10

## G7_Seq20
FC n°216
DB n°216
Stop
SQ20.Run
Seq 3A
ICB - THERMAL SHIELD COOLING
|  | Seq3A.Run And Conditionning Cryostat | [5 empty] | Seq3A.Run And Not Conditionning Cryostat
|  |  | Seq 1 |  |  |  | 6
Cryostat, conditioning He Circuit
Seq 1 ok
Testing Couplers
|  | Conditionning Couplers | [5 empty] | Not Conditionning Couplers
|  |  | Seq 2 |  |  |  | 10
Couplers, conditioning He Circuits
Seq 2 ok
Seq 3B
CRYOSTAT - THERMAL SHIELD COOLING
Seq 3B ok
Seq 5
Test Cooldown cryostat
|  | Seq5 ok And Cryostat cooldown | [5 empty] | Seq5 ok And Not Cryostat cooldown
|  |  | Seq 7 |  |  |  | 16
Cryostat, Cool Down He Circuits
Seq 7 ok
|  |  | Operations Control |  | 4K : Seq 8
2K : Seq 9
|  |  | (4K or 2K) and SHE : Seq 10 |  | Standby : Seq 11
|  | SQ20.Stopping | [6 empty] | Parameters changing
[10 empty] | Change Operations |  | 4K : Seq 8
2K : Seq 9
|  |  | Stop Operations | [6 empty] | (4K or 2K) and SHE : Seq 10 |  | Standby : Seq 11
|  |  | Test WarmUp | [5 empty] | Sequences started
|  | Sq8, Sq9, Sq10 & Sq11 Stopped | [5 empty] | 16
And WarmUp
Sq8, Sq9, Sq10 & Sq11 Stopped
|  |  | Seq 12B |  |  | And Not WarmUp
|  |  | WARM-UP CRYOSTAT |  | 22
Seq 12B ok
Test Isolated Cryostat
|  | Isolated Cryostat |  |  |  | Not Isolated Cryostat
|  |  | Seq 13 |  | 26
CRYOSTAT ISOLATED
Seq 13 ok
Test Stop Sequences
|  | Stop Sequences |  |  |  | Not Stop Sequences
|  |  | Stop Sequences |  | 0
Sq3A, Sq3B, Sq5, Sq6, Sq7, Sq8, Sq9, Sq10, Sq11 & Sq12B Stopped
0
|  |  |  | 13P091-01-3220-01-305 | [6 empty] | 2025-02-04
PAGE 20
SQ20 : SEMI-AUTOMATIC SEQUENCES
0
2
4
6
8
10
12
14
16
18
20
22
24
17
28
26