## Revision
V113
V114
V114_bis
V115
V116
V117
V118
V119
V120
V121 | 2015-06-10
V122 | 2015-08-29
V123 | 2017-02-03 | Completed the parameters in Seq 1 & 11 (no change to the PLC structure - just for documentation)
V124 | 2017-09-22 | New status fields in the Epics buffer for electrovalves, valves and heater1
V125 | 2018-01-26 | New status bits for analog signals
V126 | 2018-06-08 | New data from/to Gersemi
V127 | 2018-08-20 | New data to HNOSS PLC (General)
V128 | 2018-11-15 | New data (General) for cryomodule integration
V129 | 2018-11-20 | Added state of He exchaust change sequence.
V129 | 2019-05-02 | Added sequence parameters for the Cryomodule control
V130 | 2020-12-08 | Added magnet currents to be sent to Gersemi PLC
V131 | 2021-03-30 | Added structure for setting PID parameters from Epics (Equipments tab)
V132 | 2025-01-23 | Added extra bit for the heaters (ExtCmd), changed general parameter sParR16 to 32 boolean parameters
V133 | 2025-01-30 | Added extra bits in general parameters. Changed general parameter cParR16 to 32 boolean parameters. Added extra boolean parameter in SQ7 to automatically start SQ8. Added new boolean parameters in SQ9 to automaticaly control 2K pumps by the sequencer program. Added Gen param for PT552 from 2K pumps

## Equipments
EPICS Dialog
Digital Input | [7 empty] | All the time :
EPICS -> PLC |  |  |  | PLC -> EPICS |  |  |  |  | Copy of input is the physical input
Type "Epi_to_Plc_DI" |  |  |  | Type "Plc_to_Epi_DI" |  |  |  | Normal mode :
DBX0.0 | Bool | cmdNorm | Set Normal | DBX0.0 | Bool | sForced | Copy of Normal/Forced mode (0=Normal / 1=Forced) |  | Copy of Calculate Input is the delay input
DBX0.1 | Bool | cmdForced | Set Forced | DBX0.1 | Bool | sInp | Copy of Input | Forced mode :
DBX0.2 | Bool | cmdSet | Set forced command | DBX0.2 | Bool | sProcInp | Copy of Calculate Input |  | Copy of Calculate Input is the Forced command
DBX0.3 | Bool | cmdRst | Reset forced command | DBX0.3 | Bool
DBX0.4 | Bool |  |  | DBX0.4 | Bool
DBX0.5 | Bool |  |  | DBX0.5 | Bool
DBX0.6 | Bool |  |  | DBX0.6 | Bool
DBX0.7 | Bool |  |  | DBX0.7 | Bool
Process Analog Input
EPICS -> PLC |  |  |  | PLC -> EPICS |  |  |  |  | sRdV is always the phisical input
Type "Epi_to_Plc_AI" |  |  |  | Type "Plc_to_Epi_AI"
DBX0.0 | Bool | cmdNorm | Set Normal | DBX0.0 | Bool | sForced | Copy of Normal/Forced mode (0=Normal / 1=Forced) |  | sSetV is always a copy of Manual value
DBX0.1 | Bool | cmdForced | Set Forced | DBX0.1 | Bool | sOR | Copy of OR status (0=OK / 1=Over-range)
DBX0.2 | Bool | cmdSet | Set forced command | DBX0.2 | Bool | sUR | Copy of UR status (0=OK / 1=Under-range)
DBD2 | Real | cSetV | Manual Value | DBD2 | Real | sRdV | Process Value
|  |  |  | DBD6 | Real | sRealRdV | Real Process Values (as read from the input)
Valves | [7 empty] | Automatic mode :
EPICS -> PLC |  |  |  | PLC -> EPICS |  |  |  |  | Command is controled by program
Type "Epi_to_Plc_Valve" |  |  |  | Type "Plc_to_Epi_Valve" |  |  |  | Manual mode :
DBX0.0 | Bool | cmdAuto | Set Auto | DBX0.0 | Bool | sAuto | Copy of Auto/Manual mode (1=Auto / 0=Manual) |  | Command is controled by manual command
DBX0.1 | Bool | cmdMan | Set Manual | DBX0.1 | Bool | sSim | Copy of Simulation mode (1=Simulation)
DBX0.2 | Bool | cmdSet | Set manual command | DBX0.2 | Bool | sCmd | Copy of Command | Inhibition mode :
DBX0.3 | Bool | cmdRst | Reset manual command | DBX0.3 | Bool | sOn | Copy of On sensor(in Normal mode) - Simulated (in Simulation mode) |  | Faults are disable and sensor are simulated
DBX0.4 | Bool | cmdAck | Set Acknoledge | DBX0.4 | Bool | sOff | Copy of Off sensor(in Normal mode) - Simulated (in Simulation mode)
DBX0.5 | Bool | cmdSimSet | Set Simulation mode | DBX0.5 | Bool | sNO | Type of valve (0=Normally Closed - 1=Normally Open)
DBX0.6 | Bool | cmdSimRst | Reset Simulation mode | DBX0.6 | Bool | sOnFlt | Copy of fault On
DBX0.7 | Bool |  |  | DBX0.7 | Bool | sOffFlt | Copy of fault Off
|  |  |  | DBX1.0 | Bool | sFlt | LogicalsSum of sOnFlt and sOffFlt
|  |  |  | DBX1.1 | Bool | sCmdAuto | Copy of command in Auto mode
Electrovalves | [7 empty] | Automatic mode :
EPICS -> PLC |  |  |  | PLC -> EPICS |  |  |  |  | Command is controled by program
Type "Epi_to_Plc_EV" |  |  |  | Type "Plc_to_Epi_EV" |  |  |  | Manual mode :
DBX0.0 | Bool | cmdAuto | Set Auto | DBX0.0 | Bool | sAuto | Copy of Auto/Manual mode (1=Auto / 0=Manual) |  | Command is controled by manual command
DBX0.1 | Bool | cmdMan | Set Manual | DBX0.1 | Bool | sCmd | Copy of Command
DBX0.2 | Bool | cmdSet | Set manual command | DBX0.2 | Bool | sCmdAuto | Copy of command in Auto mode
DBX0.3 | Bool | cmdRst | Reset manual command | DBX0.3 | Bool
DBX0.4 | Bool |  |  | DBX0.4 | Bool
DBX0.5 | Bool |  |  | DBX0.5 | Bool
DBX0.6 | Bool |  |  | DBX0.6 | Bool
DBX0.7 | Bool |  |  | DBX0.7 | Bool
Analog Valves | [7 empty] | Automatic mode :
EPICS -> PLC |  |  |  | PLC -> EPICS |  |  |  |  | Output value is controled by program
Type "Epi_to_Plc_AnaValve" |  |  |  | Type "Plc_to_Epi_AnaValve" |  |  |  | Manual mode :
DBX0.0 | Bool | cmdAuto | Set Auto | DBX0.0 | Bool | sAuto | Copy of Auto/Manual mode (1=Auto / 0=Manual) |  | Output value is controled by manual value
DBX0.1 | Bool | cmdMan | Set Manual | DBX0.1 | Bool
DBX0.2 | Bool | cmdSet | Set manual command | DBX0.2 | Bool
DBD2 | Real | cSetV | Manual Value | DBD2 | Real | sRdV | Output Value
|  |  |  | DBD6 | Real | sAutoRdV | Automatic value
PID | [7 empty] | Auto mode :
EPICS -> PLC |  |  |  | PLC -> EPICS |  |  |  |  | Output mode is set to Automatic
Type "Epi_to_Plc_PID" |  |  |  | Type "Plc_to_Epi_PID" |  |  |  |  | Output value is controled by regulator with automatic Setpoint
DBX0.0 | Bool | cmdAuto | Set Auto (controlled by PLC) | DBX0.0 | Bool | sAuto | Copy of Auto/manual mode (1=Auto / 0=Manual) | Manual mode :
DBX0.1 | Bool | cmdMan | Set Norm (controlled by the operator) SPV ) | DBX0.1 | Bool | sRegOn | Copy of RegulatorOn/RegulatorOff mode (1=RegulatorOn / 0=RegulatorOff) |  | Operator can change Output mode
DBX0.2 | Bool | cmdRegOn | Set Output from setpoint via PID regulator | DBX0.2 | Bool | sAnalogSP | Copy of Analog Set-point (1 - analog setpoint, 0 - setpoint A (MKS only) |  | Output mode in RegulatorOn :
DBX0.3 | Bool | cmdRegOff | Set Output from local Output | DBX0.3 | Bool |  |  |  |  | Output value is controled by regulator with Local Setpoint
DBX0.4 | Bool | cmdSetP | Set Local Setpoint | [5 empty] | Output mode in RegulatorOff :
DBX0.5 | Bool | cmdOutput | Set Local Output | DBD2 | Real | sSetP | Actual setpoint |  |  | Output value is controled by Local Output
DBX0.6 | Bool | cmdASPon | Set Aanlog Set-poin (MKS only) | DBD6 | Real | sOutV | Actual Output
DBX0.7 | Bool | cmdASPoff | Reset Abalog Set-point (MKS only) | DBD10 | Real | sKp | Gain
DBD2 | Real | cSetP | Local Setpoint | DBD14 | Real | sTi | Integral time
DBD6 | Real | cOutput | Local Output | DBD18 | Real | sTd | Derived time
Heater (type 1) | [7 empty] | Automatic mode :
EPICS -> PLC |  |  |  | PLC -> EPICS |  |  |  |  | Command is controled by program
Type "Epi_to_Plc_Heater" |  |  |  | Type "Plc_to_Epi_Heater" |  |  |  | Manual mode :
DBX0.0 | Bool | cmdAuto | Set Auto | DBX0.0 | Bool | sAuto | Copy of Auto/Manual mode (1=Auto / 0=Manual) |  | Command is controled by manual command
DBX0.1 | Bool | cmdMan | Set Manual | DBX0.1 | Bool | sTsw | Copy of Thermoswitch
DBX0.2 | Bool | cmdSet | Set manual command | DBX0.2 | Bool | sCmd | Copy of command | All times :
DBX0.3 | Bool | cmdRst | Reset manual command | DBX0.3 | Bool | sCmdAuto | Copy of command in Auto mode |  | If Thermoswitch is ON then command is disable.
DBX0.4 | Bool | cmdHL | Set High limit | DBX0.4 | Bool | sHtrOn | State of the heater (in versions <123 sCmd behaved as this bit now)
DBX0.5 | Bool | cmdLL | Set Low Limit | DBX0.5 | Bool | sExtCmd
DBX0.6 | Bool |  |  | DBX0.6 | Bool
DBX0.7 | Bool |  |  | DBX0.7 | Bool
DBD2 | Real | cHL | High limit | DBD2 | Real | sHL | State High limit
DBD6 | Real | cLL | Low Limit | DBD6 | Real | sLL | State Low Limit
Heater (type 2) | [7 empty] | Automatic mode :
EPICS -> PLC |  |  |  | PLC -> EPICS |  |  |  |  | Commands (1, 2 & 3) are controled by program
Type "Epi_to_Plc_Heater2" |  |  |  | Type "Plc_to_Epi_Heater2" |  |  |  | Manual mode :
DBX0.0 | Bool | cmdAuto | Set Auto | DBX0.0 | Bool | sAuto | Copy of Auto/Manual mode (1=Auto / 0=Manual) |  | Commands (1, 2 & 3) are controled by manuals commands (1, 2 & 3)
DBX0.1 | Bool | cmdMan | Set Manual | DBX0.1 | Bool | sTsw | Copy of Thermoswitch
DBX0.2 | Bool | cmdSet1 | Set manual command 1 | DBX0.2 | Bool | sCmd1 | Copy of command 1 | All times :
DBX0.3 | Bool | cmdRst1 | Reset manual command 1 | DBX0.3 | Bool | sCmd2 | Copy of command 2 |  | If Thermoswitch is ON then commands are disable.
DBX0.4 | Bool | cmdSet2 | Set manual command 2 | DBX0.4 | Bool | sCmd3 | Copy of command 3
DBX0.5 | Bool | cmdRst2 | Reset manual command 2 | DBX0.5 | Bool | sLs | Copy of Water Level switch
DBX0.6 | Bool | cmdSet3 | Set manual command 3 | DBX0.6 | Bool | sHtrOn | Copy of Input Heater On
DBX0.7 | Bool | cmdRst3 | Reset manual command 3 | DBX0.7 | Bool | sSim | Copy of Simulation mode (1=Simulation)
DBX1.0 | Bool | cmdAck | Set Acknoledge | DBX1.0 | Bool | sFlt | Copy of fault
DBX1.1 | Bool | cmdSimSet | Set Simulation mode
DBX1.2 | Bool | cmdSimRst | Reset Simulation mode
DBX1.3 | Bool | cmdL1 | Set limit 1
DBX1.4 | Bool | cmdL2 | Set limit 2
DBX1.5 | Bool | cmdL3 | Set limit 3
DBX1.6 | Bool
DBX1.7 | Bool
DBD2 | Real | cL1 | limit 1 | DBD2 | Real | sL1 | limit 1
DBD6 | Real | cL2 | limit 2 | DBD6 | Real | sL2 | limit 2
DBD10 | Real | cL3 | limit 3 | DBD10 | Real | sL3 | limit 3
PLC -> EPICS
Type "Epi_to_plc_PID_Param"
DBX0.0 | Bool | cmdAuto | Not Used
DBX0.1 | Bool | cmdMan | Not Used
DBX0.2 | Bool | cmdSet1 | Not Used
DBX0.3 | Bool | cmdRst1 | Not Used
DBX0.4 | Bool | cmdSet2 | Not Used
DBX0.5 | Bool | cmdRst2 | Not Used
DBX0.6 | Bool | cmdSet3 | Not Used
DBX0.7 | Bool | cmdRst3 | Not Used
DBX1.0 | Bool | cmdAck | Not Used
DBX1.1 | Bool | cmdSimSet | Not Used
DBX1.2 | Bool | cmdSimRst | Not Used
DBX1.3 | Bool | cmdKp | Set gain (K)
DBX1.4 | Bool | cmdTi | Set Integrate time
DBX1.5 | Bool | cmdTd | Set limit diff. time
DBX1.6 | Bool
DBX1.7 | Bool
DBD2 | Real | cKp | limit 1
DBD6 | Real | cTd | limit 2
DBD10 | Real | cTi | limit 3

## Sequences
Sequences |  |  |  | SQ0 |  | SQ1 |  | SQ2 |  | SQ3A |  | SQ3B |  | SQ4 |  | SQ5 |  | SQ6 |  | SQ7 |  | SQ8 |  | SQ9 |  | SQ10 |  | SQ11 |  | SQ12A |  | SQ12B |  | SQ13 |  | SQ20
EPICS -> PLC |  |  |  | Parameter | Comment | Parameter | Comment | Parameter | Comment | Parameter | Comment | Parameter | Comment | Parameter | Comment | Parameter | Comment | Parameter | Comment | Parameter | Comment | Parameter | Comment | Parameter | Comment | Parameter | Comment | Parameter | Comment | Parameter | Comment | Parameter | Comment | Parameter | Comment | Parameter | Comment
Type "Epi_to_Plc_Seq"
DBX0.0 | Bool | cmdStart | Start - Command
DBX0.1 | Bool | cmdStop | Stop - Command
DBX0.2 | Bool | cmdPause | pause - Command | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable
DBX0.3 | Bool | cmdResume | Resume - Command | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable
DBX0.4 | Bool | cmdReset | Reset - Command
DBX0.5 | Bool | cmdAccept | Acceptation - Command
DBX0.6 | Bool | cmdSetParam | Write parameters - Commands
DBX0.7 | Bool | cmdSpare
DBX1.0 | Bool | cParB1 | Bool - Sequence parameter | [10 empty] | P_C1 | Parameter : Coupler 1 | cP_LIC100 | LIC100 pid controller (1 = ON, 0 = OFF) |  |  | P_C1 | Parameter : Cavity 1 | P_Ms | Parameter : Magnetic Shield | P_MS | Parameter : Magnetic Shield | P_C1 | Parameter : Coupler 1 | P_MS | Parameter : Magnetic Shield | P_MS |  |  |  | P_Isol_Cryo | Parameter : Isolation Cryostat (1=Cryostat isolated) | P_Cond_Cryo | Parameter : Conditionning Cryostat
DBX1.1 | Bool | cParB2 | Bool - Sequence parameter | [10 empty] | P_C2 | Parameter : Coupler 2 |  |  |  |  | P_C2 | Parameter : Cavity 2 | P_Tbl | Parameter : Table | P_Tbl | Parameter : Table | P_C2 | Parameter : Coupler 2 | P_TBL | Parameter : Table | P_Tbl | [5 empty] | P_Cond_Coupl | Parameter : Conditionning Couplers
DBX1.2 | Bool | cParB3 | Bool - Sequence parameter | [10 empty] | P_Tt | Parameter : Temperature Order |  |  |  |  | P_Tbl | Parameter : Table | cP_LIC101 | LIC101A pid controller (1 = ON, 0 = OFF) | cP_LIC101 | LIC101B pid controller (1 = ON, 0 = OFF) | P_Tt | Parameter : Temperature Order |  | Parameter : Cavity 1 | P_C1 | [5 empty] | P_Cooldown_Cryo | Parameter : Cool down Cryostat
DBX1.3 | Bool | cParB4 | Bool - Sequence parameter | [10 empty] | P_Ft | Parameter : Flow Order |  |  |  |  | P_MS | Parameter : Magnetic Shield |  |  | cP_2KpumpsAuto | Enables control of 2K pumps by seq program | P_Ft | Parameter : Flow Order |  | Parameter : Cavity 2 | P_C2 | [5 empty] | P_SHe | Parameter : Supercritique Mode
DBX1.4 | Bool | cParB5 | Bool - Sequence parameter | [16 empty] | P_StartSQ8 | Automatically start SQ8 when TRUE | [14 empty] | P_WarmUp_Cryo | Parameter : WarmUp Cryostat
DBX1.5 | Bool | cParB6 | Bool - Sequence parameter | [32 empty] | P_Isol_Cryo | Parameter : Cryostat Isolated
DBX1.6 | Bool | cParB7 | Bool - Sequence parameter | [32 empty] | P_Stop_Seq | Parameter : Stop Sequences
DBX1.7 | Bool | cParB8 | Bool - Sequence parameter
DBW2 | Int | cParI1 | Integer - Sequence parameter | P_Nb_Cycle | Parameter : Nomber of cycle to configure | P_Nb_Cycle | Parameter : Nomber of cycle to configure | P_Nb_Cycle | Parameter : Nomber of cycle to configure | [26 empty] | P_Ope_Cryo | Parameter : Operation Cryostat (1 = 4K ; 2 = 2K ; 3 = Stdy)
DBW4 | Int | cParI2 | Integer - Sequence parameter | P_Tempo_Vaccum | Parameter : Time of vaccum | P_Tempo_Vaccum | Parameter : Time of vaccum | P_Tempo_Vaccum | Parameter : Time of vaccum
DBW6 | Int | cParI3 | Integer - Sequence parameter | P_Tempo_Pressure | Parameter : Time of pressure | P_Tempo_Pressure | Parameter : Time of pressure | P_Tempo_Pressure | Parameter : Time of pressure
DBW8 | Int | cParI4 | Integer - Sequence parameter | P_Te_Al_Vaccum | Parameter : Time alarme vaccum | P_Te_Al_Vaccum | Parameter : Time alarme vaccum | P_Te_Al_Vaccum | Parameter : Time alarme vaccum
DBW10 | Int | cParI5 | Integer - Sequence parameter | P_Te_Al_Pressure | Parameter : Time alarme pressure | P_Te_Al_Pressure | Parameter : Time alarme pressure | P_Te_Al_Pressure | Parameter : Time alarme pressure
DBW12 | Int | cParI6 | Integer - Sequence parameter
DBW14 | Int | cParI7 | Integer - Sequence parameter
DBW16 | Int | Reserved8 | Integer - Sequence parameter | Not to be used by any sequence | Not to be used by any sequence | Not to be used by any sequence | Not to be used by any sequence | Not to be used by any sequence | Not to be used by any sequence | Not to be used by any sequence | Not to be used by any sequence | Not to be used by any sequence | Not to be used by any sequence | Not to be used by any sequence | Not to be used by any sequence | Not to be used by any sequence | Not to be used by any sequence | Not to be used by any sequence | Not to be used by any sequence | Not to be used by any sequence | Not to be used by any sequence | Not to be used by any sequence | Not to be used by any sequence | Not to be used by any sequence | Not to be used by any sequence | Not to be used by any sequence | Not to be used by any sequence | Not to be used by any sequence | Not to be used by any sequence | Not to be used by any sequence | Not to be used by any sequence | Not to be used by any sequence | Not to be used by any sequence | Not to be used by any sequence | Not to be used by any sequence | Not to be used by any sequence | Not to be used by any sequence
DBW18 | Int | ReservedI9 | Integer - Sequence parameter | Not to be used by any sequence
DBD20 | Real | cParR1 | Real - Sequence parameter | P_Vacum | Parameter : Pressure Vacum | P_Vacum | Parameter : Pressure Vacum | P_Vacum | Parameter : Pressure Vacum | P_Tt | Parameter : Temperature for flow cooling | P_Tt | Parameter : Temperature for flow cooling | P_CV200_Tt | Parameter : Temperature Order for control CV200 | P_PT | Parameter : Warning Pressure | P_Tt | Parametre : Temperature Security | P_PT | Parameter : Warning Pressure | P_CV550 | Parameter : Valves Order | P_CV550 | Parameter : Valves Order | P_CV301_Tt | Parameter : Temperature Order for control CV301 | P_CV550 | Parameter : Valves Order | P_WarmUp | Parameter : Temperature to Warm-Up | P_WarmUp | Parameter : Temperature Warm-Up | P_Al_SHe | Parameter : Alarme Pressure SHe Circuit
DBD24 | Real | cParR2 | Real - Sequence parameter | P_FaultVacum | Parameter : Pressure Fault Vacum | P_FaultVacum | Parameter : Pressure Fault Vacum | P_FaultVacum | Parameter : Pressure Fault Vacum | P_Low_Tt | Parameter : Low Treshold cooling | P_Low_Tt | Parameter : Low Treshold cooling (EV200) in KELVIN | P_CV200_FT | Parameter : Flow Order for control CV200 | P_FT | Parameter : Warning Flow | P_Lt | Parametre : Level Security | P_FT550 | Parameter : Warning Flow | P_LowLt | Parameter : Low Level | P_LowLt | Parameter : Low Level | P_CV301_Ft | Parameter : Flow Order for control CV301 | P_Tt | Parameter : SetPoint Temperature |  |  | P_CV550 | Parameter : Valves Order (CV550) | P_Al_He | Parameter : Alarme Pressure He Circuit
DBD28 | Real | cParR3 | Real - Sequence parameter | P_Filling | Parameter : Pressure End Of Filling GHe | P_Filling | Parameter : Pressure End Of Filling GHe | P_Filling | Parameter : Pressure End Of Filling GHe | P_High_Tt | Parameter : High Treshold cooling | P_High_Tt | Parameter : High Treshold cooling (EV200) in KELVIN | P_CV201_Tt | Parameter : Temperature Order for control CV201 | P_CV550 | Parameter : Order valve |  |  | P_Tt_Cold | Parameter : Temperature to Keeping Cold equipment | P_HighLt | Parameter : High Level | P_HighLt | Parameter : High Level | P_CV302_Tt | Parameter : Temperature Order for control CV302 | P_Pt | Parameter : Warning Pressure |  |  | P_CV551 | Parameter : Valves Order (CV551) | P_SHe | Parameter : Pressure SHe Circuit
DBD32 | Real | cParR4 | Real - Sequence parameter | P_FaultF | Parameter : Pressure Fault Filling | P_FaultF | Parameter : Pressure Fault Filling | P_FaultF | Parameter : Pressure Fault Filling |  |  |  |  | P_CV201_Ft | Parameter : Flow Order for control CV201 | P_LowLt | Parameter : Low Level |  |  | P_SP_Tt | Parameter : SetPoint Control temperature | P_Pt | Parameter : Warning Pressure | P_Pt | Parameter : Warning Pressure | P_CV302_Ft | Parameter : Flow Order for control CV302 | P_SP_Tt | Parameter : SetPoint Control Temperature |  |  | P_CV552 | Parameter : Valves Order (CV552) | P_He | Parameter : Pressure He Circuit
DBD36 | Real | cParR5 | Real - Sequence parameter |  |  | P_CV100 | Parameter : Order for Analog Valves | P_CV301 | Parameter : Order for Analog Valves | [6 empty] | P_CoolD_Tt | Parameter : Temperature cool doawn |  |  | P_CV550 | Parameter : Valves Order | P_SP_Tt | Parameter : SetPoint Control Temperature | P_SP_Tt | Parameter : SetPoint Control Temperature |  |  | P_CV551 | Parameter : Valves Order |  |  | P_CV100 | Parameter : Valves Order (CV100)
DBD40 | Real | cParR6 | Real - Sequence parameter |  |  | P_CV101 | Parameter : Order for Analog Valves | P_CV302 | Parameter : Order for Analog Valves | [6 empty] | P_HighLt | Parameter : High Level |  |  | P_CV551 | Parameter : Valves Order | P_CV551 | Parameter : Valves Order | P_CV105 | Parameter : Valves Order |  |  | P_CV552 | Parameter : Valves Order |  |  | P_CV101 | Parameter : Valves Order (CV101)
DBD44 | Real | cParR7 | Real - Sequence parameter |  |  | P_CV102 | Parameter : Order for Analog Valves | [8 empty] | P_CV100 | Parameter : Order valve |  |  | P_FT552 | Parameter : Warning Flow | P_CV552 | Parameter : Valves Order | P_CV551_Reg | Parameter - Setpoint of regulation |  |  | P_CV104 | Parameter : Valves Order |  |  | P_CV102 | Parameter : Valves Order (CV102)
DBD48 | Real | cParR8 | Real - Sequence parameter |  |  | P_CV103 | Parameter : Order for Analog Valves | [8 empty] | P_SP_LIC100 | Set Point for LIC100 pid |  |  | P_HighLt | Parameter : High Level | P_CV104 | Parameter : Valves Order | P_Final_Pt | Parameter - Final Pressure |  |  |  | Parameter : Valves Order |  |  | P_CV103 | Parameter : Valves Order (CV103)
DBD52 | Real | cParR9 | Real - Sequence parameter |  |  | P_CV104 | Parameter : Order for Analog Valves | [12 empty] | P_LowLt | Parameter : Low Level | P_SP_LIC101 | Set Point for LIC101A pid | P_SP_LIC101 | Set Point for LIC101B pid | [6 empty] | P_CV104 | Parameter : Valves Order (CV104)
DBD56 | Real | cParR10 | Real - Sequence parameter |  |  | P_CV105 | Parameter : Order for Analog Valves | [12 empty] | P_CV552 | Parameter : Valves Order | [10 empty] | P_CV105 | Parameter : Valves Order (CV105)
DBD60 | Real | cParR11 | Real - Sequence parameter |  |  | P_CV550 | Parameter : Order for Analog Valves | [12 empty] | P_CV101 | Parameter : Valves Order | [10 empty] | P_CV200 | Parameter : Valves Order (CV200)
DBD64 | Real | cParR12 | Real - Sequence parameter |  |  | P_CV551 | Parameter : Order for Analog Valves | [12 empty] | P_CV102 | Parameter : Valves Order | [10 empty] | P_CV201 | Parameter : Valves Order (CV201)
DBD68 | Real | cParR13 | Real - Sequence parameter |  |  | P_CV552 | Parameter : Order for Analog Valves | [12 empty] | P_CV103 | Parameter : Valves Order | [10 empty] | P_CV302 | Parameter : Valves Order (CV302)
DBD72 | Real | cParR14 | Real - Sequence parameter | [16 empty] | P_CV104 | Parameter : Valves Order | [10 empty] | P_CV301 | Parameter : Valves Order (CV302)
DBD76 | Real | cParR15 | Real - Sequence parameter | [16 empty] | P_CM_PT551_SP | Parameter for the Cryomodule: MKS2 set-point for the PID
DBD80 | Real | cParR16 | Real - Sequence parameter
Sequences
PLC -> EPICS
Type "Plc_to_Epi_Seq"
DBX0.0 | Bool | sActivate | Activate - State
DBX0.1 | Bool | sRun | Run - State
DBX0.2 | Bool | sPause | Pause - State
DBX0.3 | Bool | sFault | Fault - State
DBX0.4 | Bool | sStop | Stop - State
DBX0.5 | Bool | sStopping | Stopping - State
DBX0.6 | Bool | sCIok | Initials conditions ok
DBX0.7 | Bool | sCSok | Security conditions ok
DBX1.0 | Bool | sFlt1 | Sequence Fault | Flt_Vaccum | Fault : Vaccum Alarm | Flt_Vaccum | Fault : Vaccum Alarm | Flt_Vaccum | Fault : Vaccum Alarm | [24 empty] | Flt_SHePres | Fault : Circuits SHe Pressure
DBX1.1 | Bool | sFlt2 | Sequence Fault | Flt_Pressure | Fault : Vaccum Alarm | Flt_Pressure | Fault : Vaccum Alarm | Flt_Pressure | Fault : Vaccum Alarm | [24 empty] | Flt_HePres | Fault : Circuits He Pressure
DBX1.2 | Bool | sFlt3 | Sequence Fault
DBX1.3 | Bool | sFlt4 | Sequence Fault
DBX1.4 | Bool | sFlt5 | Sequence Fault
DBX1.5 | Bool | sFlt6 | Sequence Fault
DBX1.6 | Bool | sCheckParam | Check Parameters
DBX1.7 | Bool | sCheckEquip | Check Equipment in manual mode
DBW2 | Int | sStep | Sequence Grafcet Step
DBW4 | Int | sStepTime | Temporisation of Sequence Grafcet Step | [6 empty] | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable
DBW6 | Int | sStateI1 | Integer - State indicator | Cpt_Nb_Cycle | Compteur : Actual Nomber of cycle | Cpt_Nb_Cycle | Compteur : Actual Nomber of cycle | Cpt_Nb_Cycle | Compteur : Actual Nomber of cycle
DBW8 | Int | sStateI2 | Integer - State indicator
DBD10 | Real | sStateR1 | Real - State indicator
DBD14 | Real | sStateR2 | Real - State indicator
DBX18.0 | Bool | sParB1 | Bool - Sequence parameter | Same as Epics to Plc commands parameters
DBX18.1 | Bool | sParB2 | Bool - Sequence parameter
DBX18.2 | Bool | sParB3 | Bool - Sequence parameter
DBX18.3 | Bool | sParB4 | Bool - Sequence parameter
DBX18.4 | Bool | sParB5 | Bool - Sequence parameter
DBX18.5 | Bool | sParB6 | Bool - Sequence parameter
DBX18.6 | Bool | sParB7 | Bool - Sequence parameter
DBX18.7 | Bool | sParB8 | Bool - Sequence parameter
DBW20 | Int | sParI1 | Integer - Sequence parameter
DBW22 | Int | sParI2 | Integer - Sequence parameter
DBW24 | Int | sParI3 | Integer - Sequence parameter
DBW26 | Int | sParI4 | Integer - Sequence parameter
DBW28 | Int | sParI5 | Integer - Sequence parameter
DBW30 | Int | sParI6 | Integer - Sequence parameter
DBW32 | Int | sParI7 | Integer - Sequence parameter
DBW34 | Int | sHiddenFlags | Sequence - hidden flags
DBW36 | Int | sInitCond | Sequence - Initials conditions
DBD38 | Real | sParR1 | Real - Sequence parameter
DBD42 | Real | sParR2 | Real - Sequence parameter
DBD46 | Real | sParR3 | Real - Sequence parameter
DBD50 | Real | sParR4 | Real - Sequence parameter
DBD54 | Real | sParR5 | Real - Sequence parameter
DBD58 | Real | sParR6 | Real - Sequence parameter
DBD62 | Real | sParR7 | Real - Sequence parameter
DBD66 | Real | sParR8 | Real - Sequence parameter
DBD70 | Real | sParR9 | Real - Sequence parameter
DBD74 | Real | sParR10 | Real - Sequence parameter
DBD78 | Real | sParR11 | Real - Sequence parameter
DBD82 | Real | sParR12 | Real - Sequence parameter
DBD86 | Real | sParR13 | Real - Sequence parameter
DBD90 | Real | sParR14 | Real - Sequence parameter
DBD94 | Real | sParR15 | Real - Sequence parameter
DBD98 | Real | sParR16 | Real - Sequence parameter

## General
General
EPICS -> PLC
Type "Epi_to_Plc_Gen"
DBX0.0 | Bool | cmdSetParam | Write parameters - Commands
DBX0.1 | Bool | CmdSetAck | Set General Acknoledge - Commands
DBX0.2 | Bool | cmdSet2KtoBaloon | Direct the 2K He recirculation to the Baloon
DBX0.3 | Bool | cmdRst2KtoBaloon | Direct the 2K He recirculation to the compressor
DBX0.4 | Bool | cmdSet4KtoBaloon | Direct the 4K He recirculation to the Baloon
DBX0.5 | Bool | cmdRst4KtoBaloon | Direct the 4K He recirculation to the compressor
DBX0.6 | Bool | cmdSetCMmode | Set Cryo-module mode
DBX0.7 | Bool | cmdRstCMmode | Reset Cryo-module mode (return to HNOSS mode)
DBX1.0 | Bool | Dwr:CW5202_open | Status of Linde's CV5202 1 -open, 0 - closed
DBX1.1 | Bool | Dwr:CW5201_open | Status of Linde's CV5201 1 -open, 0 - closed
DBX1.2 | Bool | PB_com_2Kpumps | Status of PB comm. to 2K pumps 1-OK, 0- error
DBX1.3 | Bool | WTRVAC_IOC | 1- connected, 0 - disconnected
DBX1.4 | Bool | WTRVAC_IOC_STAT | 1 - OK, 0 - error
DBX1.5 | Bool | cmdSetLocal | Set Local mode (WinCC control)
DBX1.6 | Bool | cmdSetRemote | Set Remote mode (Epics control)
DBX1.7 | Bool | cParB8 | Bool - Dialogue
DBW2 | Int | HBcounter | HeartBeat counter from Gersemi (updates at least every 10 s)
DBW4 | Int | HBcounter-ioc | HearBeat counter from HNOSS ioc
DBW6 | Int | PC1_Cur_SEVR | Severity status of MAG-RCH1:I_MEAS
DBW8 | Int | PC2_Cur_SEVR | Severity status of MAG-RCH2:I_MEAS
DBW10 | Int | cParI5 | Integer - Dialogue
DBW12 | Int | cParI6 | Integer - Dialogue
DBW14 | Int | cParI7 | Integer - Dialogue
DBW16 | Int | cParI8 | Integer - Dialogue
DBW18 | Int | cParI9 | Integer - Dialogue
DBD20 | Real | LI5200-PercOut | LHe level in the dewar
DBD24 | Real | LI3685-PercOut | LN2 level in the tank
DBD28 | Real | UY5202-PercOut | Percentage of opening of the dewar valve
DBD32 | Real | Freq_2K_pumps | Mean revol. Freq. of all 2K pumps Hz | Note: for this value to be trusted the following condition must be true:
DBD36 | Real | UY5201-PercOut | Percentage of opening of the dewar valve | (PB_com_2Kpumps = 1) & (WTRVAC_IOC = 1) & (WTRVAC_IOC_STAT = 1) & (HBcounter-ioc MUST change every 10 s)
DBD40 | Real | PC1_CURRENT | Magnet current MAG-RCH1:I_MEAS
DBD44 | Real | PC2_CURRENT | Magnet current MAG-RCH2:I_MEAS
DBD48 | Real | PT552_2K_pumps | PT552 from 2K pumps (wtrvac IOC)
DBD52 | Real | cParR9 | Real - Dialogue
DBD56 | Real | cParR10 | Real - Dialogue
DBD60 | Real | cParR11 | Real - Dialogue
DBD64 | Real | cParR12 | Real - Dialogue
DBD68 | Real | cParR13 | Real - Dialogue
DBD72 | Real | cParR14 | Real - Dialogue
DBD76 | Real | cParR15 | Real - Dialogue
DBX80.0 | Bool | cmdSetStdCnx | Select standard set of Cernox for cavities
DBX80.1 | Bool | cmdSetAltCnx | Select alternative set of Cernox for cavities
DBX80.2 | Bool | cmdUpdCnxCalibr | Updated Cernox calibration (possible only when standard set)
DBX80.3 | Bool | cXparB4 | Bool - Dialog
DBX80.4 | Bool | cXparB5 | Bool - Dialog
DBX80.5 | Bool | cXparB6 | Bool - Dialog
DBX80.6 | Bool | cXparB7 | Bool - Dialog
DBX80.7 | Bool | cXparB8 | Bool - Dialog
DBX80.8 | Bool | cXparB9 | Bool - Dialog
DBX80.9 | Bool | cXparB10 | Bool - Dialog
DBX80.10 | Bool | cXparB11 | Bool - Dialog
DBX80.11 | Bool | cXparB12 | Bool - Dialog
DBX80.12 | Bool | cXparB13 | Bool - Dialog
DBX80.13 | Bool | cXparB14 | Bool - Dialog
DBX80.14 | Bool | cXparB15 | Bool - Dialog
DBX80.15 | Bool | cXparB16 | Bool - Dialog
DBX80.16 | Bool | cXparB17 | Bool - Dialog
DBX80.17 | Bool | cXparB18 | Bool - Dialog
DBX80.18 | Bool | cXparB19 | Bool - Dialog
DBX80.19 | Bool | cXparB20 | Bool - Dialog
DBX80.20 | Bool | cXparB21 | Bool - Dialog
DBX80.21 | Bool | cXparB22 | Bool - Dialog
DBX80.22 | Bool | cXparB23 | Bool - Dialog
DBX80.23 | Bool | cXparB24 | Bool - Dialog
DBX80.24 | Bool | cXparB25 | Bool - Dialog
DBX80.25 | Bool | cXparB26 | Bool - Dialog
DBX80.26 | Bool | cXparB27 | Bool - Dialog
DBX80.27 | Bool | cXparB28 | Bool - Dialog
DBX80.28 | Bool | cXparB29 | Bool - Dialog
DBX80.29 | Bool | cXparB30 | Bool - Dialog
DBX80.30 | Bool | cXparB31 | Bool - Dialog
DBX80.31 | Bool | cXparB32 | Bool - Dialog
General
PLC -> EPICS
Type "Plc_to_Epi_Gen"
DBX0.0 | Bool | sLocal | false - EPICS rules, true - WinCC is in charge
DBX0.1 | Bool | s2KtoBaloon | false compressor, true - gas baloon
DBX0.2 | Bool | s4KtoBaloon | false compressor, true - gas baloon
DBX0.3 | Bool | sCMmode | 1 - Cryo-module mode, 0 - HNOSS mode
DBX0.4 | Bool | sCV5202OpenReq | 1 - request to open CV5202
DBX0.5 | Bool
DBX0.6 | Bool
DBX0.7 | Bool
DBX1.0 | Bool | sParB1 | Bool - Dialogue
DBX1.1 | Bool | sParB2 | Bool - Dialogue
DBX1.2 | Bool | sParB3 | Bool - Dialogue
DBX1.3 | Bool | sParB4 | Bool - Dialogue
DBX1.4 | Bool | sParB5 | Bool - Dialogue
DBX1.5 | Bool | sParB6 | Bool - Dialogue
DBX1.6 | Bool | sParB7 | Bool - Dialogue
DBX1.7 | Bool | sParB8 | Bool - Dialogue
DBW2 | Int | sGersemi_HB | Life_Word from Gersemi
DBW4 | Int | sState_4K_X | Step of the 4K exhaust change between compressor and gas bag
DBW6 | Int | sState_2K_X | Step of the 2K exhaust change between compressor and gas bag
DBW8 | Int | sParI4 | Integer - Dialogue
DBW10 | Int | sParI5 | Integer - Dialogue
DBW12 | Int | sParI6 | Integer - Dialogue
DBW14 | Int | sParI7 | Integer - Dialogue
DBW16 | Int | sParI8 | Integer - Dialogue
DBW18 | Int | sParI9 | Integer - Dialogue
DBD20 | Real | sParR1 | Real - Dialogue
DBD24 | Real | sParR2 | Real - Dialogue
DBD28 | Real | sParR3 | Real - Dialogue
DBD32 | Real | sParR4 | Real - Dialogue
DBD36 | Real | sParR5 | Real - Dialogue
DBD40 | Real | sParR6 | Real - Dialogue
DBD44 | Real | sParR7 | Real - Dialogue
DBD48 | Real | sParR8 | Real - Dialogue
DBD52 | Real | sParR9 | Real - Dialogue
DBD56 | Real | sParR10 | Real - Dialogue
DBD60 | Real | sParR11 | Real - Dialogue
DBD64 | Real | sParR12 | Real - Dialogue
DBD68 | Real | sParR13 | Real - Dialogue
DBD72 | Real | sParR14 | Real - Dialogue
DBD76 | Real | sParR15 | Real - Dialogue
DBX80.0 | Bool | sFV560_OpenReq | Request to open FV560 (1 - open, 0 - close)
DBX80.1 | Bool | sFV561_OpenReq | Request to open FV561 (1 - open, 0 - close)
DBX80.2 | Bool | sFV562_OpenReq | Request to open FV562 (1 - open, 0 - close)
DBX80.3 | Bool | sFV563_OpenReq | Request to open FV563 (1 - open, 0 - close)
DBX80.4 | Bool | sStdCernox | Standard Cernox set connected to the cavities
DBX80.5 | Bool | sXParB6 | Bool - Dialogue
DBX80.6 | Bool | sXParB7 | Bool - Dialogue
DBX80.7 | Bool | sXParB8 | Bool - Dialogue
DBX80.8 | Bool | sXParB9 | Bool - Dialogue
DBX80.9 | Bool | sXParB10 | Bool - Dialogue
DBX80.10 | Bool | sXParB11 | Bool - Dialogue
DBX80.11 | Bool | sXParB12 | Bool - Dialogue
DBX80.12 | Bool | sXParB13 | Bool - Dialogue
DBX80.13 | Bool | sXParB14 | Bool - Dialogue
DBX80.14 | Bool | sXParB15 | Bool - Dialogue
DBX80.15 | Bool | sXParB16 | Bool - Dialogue
DBX80.16 | Bool | sXParB17 | Bool - Dialogue
DBX80.17 | Bool | sXParB18 | Bool - Dialogue
DBX80.18 | Bool | sXParB19 | Bool - Dialogue
DBX80.19 | Bool | sXParB20 | Bool - Dialogue
DBX80.20 | Bool | sXParB21 | Bool - Dialogue
DBX80.21 | Bool | sXParB22 | Bool - Dialogue
DBX80.22 | Bool | sXParB23 | Bool - Dialogue
DBX80.23 | Bool | sXParB24 | Bool - Dialogue
DBX80.24 | Bool | sXParB25 | Bool - Dialogue
DBX80.25 | Bool | sXParB26 | Bool - Dialogue
DBX80.26 | Bool | sXParB27 | Bool - Dialogue
DBX80.27 | Bool | sXParB28 | Bool - Dialogue
DBX80.28 | Bool | sXParB29 | Bool - Dialogue
DBX80.29 | Bool | sXParB30 | Bool - Dialogue
DBX80.30 | Bool | sXParB31 | Bool - Dialogue
DBX80.31 | Bool | sXParB32 | Bool - Dialogue

## Parameters
Real Parameters |  |  |  | SQ9_CV551_PT |  | SQ9_CV551_Csg
EPICS -> PLC |  |  |  | Parameter | Comment | Parameter | Comment
Type "Epi_to_Plc_ParR"
DBD0 | Real | cParR0 | Real - Dialogue | PT00 | Pressure limit | Csg00 | Setpoint of analog valve
DBD4 | Real | cParR1 | Real - Dialogue | PT01 | Pressure limit | Csg01 | Setpoint of analog valve
DBD8 | Real | cParR2 | Real - Dialogue | PT02 | Pressure limit | Csg02 | Setpoint of analog valve
DBD12 | Real | cParR3 | Real - Dialogue | PT03 | Pressure limit | Csg03 | Setpoint of analog valve
DBD16 | Real | cParR4 | Real - Dialogue | PT04 | Pressure limit | Csg04 | Setpoint of analog valve
DBD20 | Real | cParR5 | Real - Dialogue | PT05 | Pressure limit | Csg05 | Setpoint of analog valve
DBD24 | Real | cParR6 | Real - Dialogue | PT06 | Pressure limit | Csg06 | Setpoint of analog valve
DBD28 | Real | cParR7 | Real - Dialogue | PT07 | Pressure limit | Csg07 | Setpoint of analog valve
DBD32 | Real | cParR8 | Real - Dialogue | PT08 | Pressure limit | Csg08 | Setpoint of analog valve
DBD36 | Real | cParR9 | Real - Dialogue | PT09 | Pressure limit | Csg09 | Setpoint of analog valve
DBD40 | Real | cParR10 | Real - Dialogue | PT010 | Pressure limit | Csg010 | Setpoint of analog valve
DBD44 | Real | cParR11 | Real - Dialogue | PT011 | Pressure limit | Csg011 | Setpoint of analog valve
DBD48 | Real | cParR12 | Real - Dialogue | PT012 | Pressure limit | Csg012 | Setpoint of analog valve
DBD52 | Real | cParR13 | Real - Dialogue
DBD56 | Real | cParR14 | Real - Dialogue
DBD60 | Real | cParR15 | Real - Dialogue
Real Parameters
PLC -> EPICS
Type "Plc_to_Epi_ParR"
DBD0 | Real | sParR0 | Real - Dialogue | PT00 | Pressure limit | Csg00 | Setpoint of analog valve
DBD4 | Real | sParR1 | Real - Dialogue | PT01 | Pressure limit | Csg01 | Setpoint of analog valve
DBD8 | Real | sParR2 | Real - Dialogue | PT02 | Pressure limit | Csg02 | Setpoint of analog valve
DBD12 | Real | sParR3 | Real - Dialogue | PT03 | Pressure limit | Csg03 | Setpoint of analog valve
DBD16 | Real | sParR4 | Real - Dialogue | PT04 | Pressure limit | Csg04 | Setpoint of analog valve
DBD20 | Real | sParR5 | Real - Dialogue | PT05 | Pressure limit | Csg05 | Setpoint of analog valve
DBD24 | Real | sParR6 | Real - Dialogue | PT06 | Pressure limit | Csg06 | Setpoint of analog valve
DBD28 | Real | sParR7 | Real - Dialogue | PT07 | Pressure limit | Csg07 | Setpoint of analog valve
DBD32 | Real | sParR8 | Real - Dialogue | PT08 | Pressure limit | Csg08 | Setpoint of analog valve
DBD36 | Real | sParR9 | Real - Dialogue | PT09 | Pressure limit | Csg09 | Setpoint of analog valve
|  |  |  | PT010 | Pressure limit | Csg010 | Setpoint of analog valve
|  |  |  | PT011 | Pressure limit | Csg011 | Setpoint of analog valve
|  |  |  | PT012 | Pressure limit | Csg012 | Setpoint of analog valve

## Alarm
Bool Alarm
PLC -> Epics
Type "Plc_to_Epi_Alarm"
DBX0.0 | Bool | Al1 | Alarm | F_pilz | Fault on emergency stop
DBX0.1 | Bool | Al2 | Alarm | F_J000 | Fault on Vaccum pumping system J000 | No connected to the PLC
DBX0.2 | Bool | Al3 | Alarm | F_J001 | Fault on Vaccum pumping system J001 | No connected to the PLC
DBX0.3 | Bool | Al4 | Alarm | F_P000 | Fault on Vaccum pump P000 | No connected to the PLC
DBX0.4 | Bool | Al5 | Alarm | F_SH300 | Fault on supercritical helium production | No connected to the PLC
DBX0.5 | Bool | Al6 | Alarm | MKS1.Fault/Send | Fault on data Send
DBX0.6 | Bool | Al7 | Alarm | MKS1.Fault/Recv | Fault on data Receive
DBX0.7 | Bool | Al8 | Alarm | MKS1.Fault/Local_mode | Fault Local mode
DBX1.0 | Bool | Al9 | Alarm | MKS1.Fault/Learning | Fault Learning
DBX1.1 | Bool | Al10 | Alarm | MKS1.Fault/SP_Control | Fault on Setpoint Control
DBX1.2 | Bool | Al11 | Alarm | MKS1.Fault/Wr_SP_Type0 | Fault on Writing of Type0 Setpoint
DBX1.3 | Bool | Al12 | Alarm | MKS1.Fault/Wr_SP_Type1 | Fault on Writing of Type1 Setpoint
DBX1.4 | Bool | Al13 | Alarm | MKS1.Fault/Wr_SP | Fault on Setpoint writing
DBX1.5 | Bool | Al14 | Alarm | MKS1.Fault/Wr_SP_Sel | Fault on setpoint selection writing
DBX1.6 | Bool | Al15 | Alarm | MKS1.Fault/Wr_Kp | Fault on Kp writing
DBX1.7 | Bool | Al16 | Alarm | MKS1.Fault/Wr_Ti | Fault on Ti writing
DBX2.0 | Bool | Al17 | Alarm | MKS1.Fault/Wr_Out_Val | Fault on Out_Val writing
DBX2.1 | Bool | Al18 | Alarm | MKS1.Fault/Wr_PT01 | Fault on PT01 Writing
DBX2.2 | Bool | Al19 | Alarm | MKS1.Fault/Wr_Status | Fault on Status wrinting
DBX2.3 | Bool | Al20 | Alarm | MKS1.Fault/Verif_SP_Type0 | Fault on Setpoint Type0 checking
DBX2.4 | Bool | Al21 | Alarm | MKS1.Fault/Verif_SP_Type1 | Fault on Setpoint Type1 checking
DBX2.5 | Bool | Al22 | Alarm | MKS1.Fault/Verif_SP | Fault on Setpoint checking
DBX2.6 | Bool | Al23 | Alarm | MKS1.Fault/Verif_SP_Sel | Fault on Setpoint Selection checking
DBX2.7 | Bool | Al24 | Alarm | MKS1.Fault/Verif_Kp | Fault on Kp checking
DBX3.0 | Bool | Al25 | Alarm | MKS1.Fault/Verif_Ti | Fault on Ti checking
DBX3.1 | Bool | Al26 | Alarm | MKS1.Fault/Verif_Out_Val | Fault on Out_Val checking
DBX3.2 | Bool | Al27 | Alarm | MKS1.Fault/Verif_PT01 | Fault on PT01 checking
DBX3.3 | Bool | Al28 | Alarm | MKS1.Fault/Verif_Status | Fault on Status checking
DBX3.4 | Bool | Al29 | Alarm | MKS2.Fault/Send | Fault on data Send
DBX3.5 | Bool | Al30 | Alarm | MKS2.Fault/Recv | Fault on data Receive
DBX3.6 | Bool | Al31 | Alarm | MKS2.Fault/Local_mode | Fault Local mode
DBX3.7 | Bool | Al32 | Alarm | MKS2.Fault/Learning | Fault Learning
DBX4.0 | Bool | Al33 | Alarm | MKS2.Fault/SP_Control | Fault on Setpoint Control
DBX4.1 | Bool | Al34 | Alarm | MKS2.Fault/Wr_SP_Type0 | Fault on Writing of Type0 Setpoint
DBX4.2 | Bool | Al35 | Alarm | MKS2.Fault/Wr_SP_Type1 | Fault on Writing of Type1 Setpoint
DBX4.3 | Bool | Al36 | Alarm | MKS2.Fault/Wr_SP | Fault on Setpoint writing
DBX4.4 | Bool | Al37 | Alarm | MKS2.Fault/Wr_SP_Sel | Fault on setpoint selection writing
DBX4.5 | Bool | Al38 | Alarm | MKS2.Fault/Wr_Kp | Fault on Kp writing
DBX4.6 | Bool | Al39 | Alarm | MKS2.Fault/Wr_Ti | Fault on Ti writing
DBX4.7 | Bool | Al40 | Alarm | MKS2.Fault/Wr_Out_Val | Fault on Out_Val writing
DBX5.0 | Bool | Al41 | Alarm | MKS2.Fault/Wr_PT01 | Fault on PT01 Writing
DBX5.1 | Bool | Al42 | Alarm | MKS2.Fault/Wr_Status | Fault on Status wrinting
DBX5.2 | Bool | Al43 | Alarm | MKS2.Fault/Verif_SP_Type0 | Fault on Setpoint Type0 checking
DBX5.3 | Bool | Al44 | Alarm | MKS2.Fault/Verif_SP_Type1 | Fault on Setpoint Type1 checking
DBX5.4 | Bool | Al45 | Alarm | MKS2.Fault/Verif_SP | Fault on Setpoint checking
DBX5.5 | Bool | Al46 | Alarm | MKS2.Fault/Verif_SP_Sel | Fault on Setpoint Selection checking
DBX5.6 | Bool | Al47 | Alarm | MKS2.Fault/Verif_Kp | Fault on Kp checking
DBX5.7 | Bool | Al48 | Alarm | MKS2.Fault/Verif_Ti | Fault on Ti checking
DBX6.0 | Bool | Al49 | Alarm | MKS2.Fault/Verif_Out_Val | Fault on Out_Val checking
DBX6.1 | Bool | Al50 | Alarm | MKS2.Fault/Verif_PT01 | Fault on PT01 checking
DBX6.2 | Bool | Al51 | Alarm | MKS2.Fault/Verif_Status | Fault on Status checking
DBX6.3 | Bool | Al52 | Alarm | MKS3.Fault/Send | Fault on data Send
DBX6.4 | Bool | Al53 | Alarm | MKS3.Fault/Recv | Fault on data Receive
DBX6.5 | Bool | Al54 | Alarm | MKS3.Fault/Local_mode | Fault Local mode
DBX6.6 | Bool | Al55 | Alarm | MKS3.Fault/Learning | Fault Learning
DBX6.7 | Bool | Al56 | Alarm | MKS3.Fault/SP_Control | Fault on Setpoint Control
DBX7.0 | Bool | Al57 | Alarm | MKS3.Fault/Wr_SP_Type0 | Fault on Writing of Type0 Setpoint
DBX7.1 | Bool | Al58 | Alarm | MKS3.Fault/Wr_SP_Type1 | Fault on Writing of Type1 Setpoint
DBX7.2 | Bool | Al59 | Alarm | MKS3.Fault/Wr_SP | Fault on Setpoint writing
DBX7.3 | Bool | Al60 | Alarm | MKS3.Fault/Wr_SP_Sel | Fault on setpoint selection writing
DBX7.4 | Bool | Al61 | Alarm | MKS3.Fault/Wr_Kp | Fault on Kp writing
DBX7.5 | Bool | Al62 | Alarm | MKS3.Fault/Wr_Ti | Fault on Ti writing
DBX7.6 | Bool | Al63 | Alarm | MKS3.Fault/Wr_Out_Val | Fault on Out_Val writing
DBX7.7 | Bool | Al64 | Alarm | MKS3.Fault/Wr_PT01 | Fault on PT01 Writing
DBX8.0 | Bool | Al65 | Alarm | MKS3.Fault/Wr_Status | Fault on Status wrinting
DBX8.1 | Bool | Al66 | Alarm | MKS3.Fault/Verif_SP_Type0 | Fault on Setpoint Type0 checking
DBX8.2 | Bool | Al67 | Alarm | MKS3.Fault/Verif_SP_Type1 | Fault on Setpoint Type1 checking
DBX8.3 | Bool | Al68 | Alarm | MKS3.Fault/Verif_SP | Fault on Setpoint checking
DBX8.4 | Bool | Al69 | Alarm | MKS3.Fault/Verif_SP_Sel | Fault on Setpoint Selection checking
DBX8.5 | Bool | Al70 | Alarm | MKS3.Fault/Verif_Kp | Fault on Kp checking
DBX8.6 | Bool | Al71 | Alarm | MKS3.Fault/Verif_Ti | Fault on Ti checking
DBX8.7 | Bool | Al72 | Alarm | MKS3.Fault/Verif_Out_Val | Fault on Out_Val checking
DBX9.0 | Bool | Al73 | Alarm | MKS3.Fault/Verif_PT01 | Fault on PT01 checking
DBX9.1 | Bool | Al74 | Alarm | MKS3.Fault/Verif_Status | Fault on Status checking
DBX9.2 | Bool | Al75 | Alarm | Linde_LHe_LI_OK | Lhe level in the dewar ok
DBX9.3 | Bool | Al76 | Alarm | CV5202_Intrlck | Allow to open the valve
DBX9.4 | Bool | Al77 | Alarm
DBX9.5 | Bool | Al78 | Alarm
DBX9.6 | Bool | Al79 | Alarm
DBX9.7 | Bool | Al80 | Alarm